## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-PEDCO-120-PI-MT-0008 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2615 |  |  | Transmital Date:3/2/2024
Document Title: MTO For Insulation |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PI-TR-2615 |  |  | Transmital Date:3/2/2024
[5 empty] | CRS No:PEDCO-CRS-BK-GCS-PEDCO-120-PI-MT-0008_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مشخصات Insulation ها بايستي مطابق با Specification For Insulation و Line List باشد كه در مدرك رعايت نشده است بطور مثال مطابق مدارك Line List و Specification for Insulation ضخامت عايق براي خطوط 6 اينچ بايستي 60mm باشد ولي در MTO ضخامت 40mm ذكر شده است. همچنين بعلت نهايي نشدن مدل PDMS و عدم ارائه نقشه هاي ايزومتريك مشخص كردن طول INSULATION مقدور نمي باشد كه در نهايت تهيه مقدار مورد نياز بعهده پيمانكار مي باشد. |  | BK-SUR-ENG-PIP-02-09074 | 2024-03-04 | مدرک ویرایش شد. لازم به ذکر است که سایز 6 اینچ شامل دو ضخامت برای عایق جرارتی و حفاظت پرسنل می باشد. |  |  | closed
2 | در مدرك MTO عايق براي لوله سايز 8 اينچ ذكر شده است در حاليكه مطابق P&ID و Line List لوله سايز 8 اينچ كه نياز به عايق داشته باشد نداريم. لذا بررسي و اصلاحات لازم اعمال گردد. |  | BK-SUR-ENG-PIP-02-09074 | 2024-03-04 | سایز 8 اینچ در لاین لیست عایق دارد. (حفاظت پرسنل) |  |  | closed
3 | از انجا که مسئولیت طراحی تفصیلی پروژه برعهده ی پیمانکار است،لذا مدارک MTO تهیه شده جهت اطلاع کارفرما محسوب میشود و میبایست براساس نتایج مدل سه بعدی و مطابق با مشخصات استانداردی مورد تایید تهیه گردد،لذا از آنجا که مبنای براورد کالا مشخص نیست،ارسال این مدارک با این شرایط یک اقدام زود هنگام به شمار می آید و قابل صحت سنجی نیست.لازم به ذکر است مسئولیت کامل بروز هرگونه تناقض(مشخصات و یا تعداد) در هر مرحله از پروژه به عهده پیمانکار است. |  | BK-SUR-ENG-PIP-02-09074 | 2024-03-04 | احتراما مدل سه بعدی90% ایستگاه تقویت فشار مطابق جلسات مربوطه برگزار شده تهیه و برای کارفرمای محترم ارسال شده است و این مدرک برآن اساس و مطابق مشخصات استانداردی تهیه شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date :