## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ESD CONSOLE/ F&G MATRIX PANEL
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 9
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0017 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR ESD CONSOLE/ F&G MATRIX PANEL نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | MAY.2024 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D02 |  | NOV.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D01 |  | DEC.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | APR.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F9Z-708937
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ESD CONSOLE/ F&G MATRIX PANEL
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 9
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0017 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | X | [5 empty] | 67
4 | X | X | X |  | X |  |  |  | 68
5 | X | X | X |  | X |  |  |  | 69
6 | X | X | X |  | X |  |  |  | 70
7 | X | X | X |  | X |  |  |  | 71
8 |  | X | X |  | X |  |  |  | 72
9 |  |  |  |  | X |  |  |  | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ESD CONSOLE/ F&G MATRIX PANEL
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 9
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0017 | D03
REFERENCE DOCUMENTS :
|  | ESD PHILOSOPHY | [6 empty] | BK-GCS-PEDCO-120-PR-PH-0005
|  | I/O LIST FOR ESD SYSTEM | [6 empty] | BK-GCS-PEDCO-120-IN-LI-0003
|  | I/O LIST FOR F&G SYSTEM | [6 empty] | BK-GCS-PEDCO-120-IN-LI-0004
|  | F&G LOCATION LAYOUT FOR PROCESS AREA | [6 empty] | BK-GCS-PEDCO-120-IN-PY-0005
|  | F&G LOCATION LAYOUT FOR BUILDINGS | [6 empty] | BK-GCS-PEDCO-120-IN-PY-0006
|  | CAUSE & EFFECT DIAGRAM | [6 empty] | BK-GCS-PEDCO-120-PR-CE-0001
|  | F&G CAUSE AND EFFECT DIAGRAM FOR PROCESS AREA | [6 empty] | BK-GCS-PEDCO-120-IN-DG-0009
|  | F&G CAUSE AND EFFECT DIAGRAM FOR BUILDINGS | [6 empty] | BK-GCS-PEDCO-120-IN-DG-0010
|  | ESD LEVEL HIERARCHY | [6 empty] | BK-GCS-PEDCO-120-IN-DG-0003

## ESD CONSOLE
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ESD CONSOLE/ F&G MATRIX PANEL
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 9
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | IN | DT | 0017 | D03
ESD CONSOLE
| DIMENSION | [5 empty] | 120X75 cm2 (Refer to the Attachment)
| THICKNESS | [5 empty] | 3 MM
| NUMBER OF BUTTONS FOR ESD CONSOLE | [5 empty] | 3 PUSH BUTTON, + 12 MUSHROOM HEAD LATCH (LOCKABLE) P.B. WITH PROTECTION COVER + 1 SELECTOR SWITCH WITH KEY
| NUMBER OF LAMPS FOR ESD CONSOLE | [5 empty] | 13
| LAMP COLOR FOR ESD CONSOLE | [5 empty] | Red
| BUTTON TYPE | [5 empty] | PUSH BUTTON, MUSHROOM HEAD LATCH (LOCKABLE) P.B. WITH PROTECTION COVER, SELECTOR SWITCH 2 POSITION WITH KEY (S.B.2)
| INGRESS PROTECTION | [5 empty] | IP54
| MATERIAL | [5 empty] | SHEET STEEL (According to manufacturer/supplier’s own standards)
| CONSOLE COLOR | [5 empty] | RAL 7035
| ACCESS | [5 empty] | FRONT and REAR (VTC)
| CABLE ENTRY | [5 empty] | FROM CONSOLE BOTTOM
| CONSOLE CONTENT | [5 empty] | ALARM ANNUNCIATE, PUSH BUTTONS, INDICATING LAMPS and N.I.S. I/O TERMINATION
| POWER RANGE | [5 empty] | 24 VDC
NOTES: 1- REQUIRED TERMINALS SHALL BE CONSIDERED TO CONNECT ESD CONSOLE TO ESD SYSTEMS. 2- SUITABLE GLAND WITH SPARE PLUGGED CABLE ENTRIES TO BE CONSIDERED. 3- PUSH BUTTONS AND LAMPS SHALL BE CONSIDERED. 4- 20% SPARE BUTTONS AND LAMPS (NOT CONNECTED) SHALL BE CONSIDERED ON THE CONSOLE. 5- SPARE PARTS FOR COMMISSIONING AND 2 YEARS TO BE PROVIDED. 6- IN ORDER TO HAVE AUDIBLE ALARM HORN TO BE CONSIDERED . 7- IF ANY RELAY, BARRIER AND OTHER DEVICES ARE REQUIRED IN THE ESD CONSOLE, IT SHALL BE SIL3. 8- ARRANGMENT OF THE PUSH BUTTONS AND LAMPS SHALL BE BASED ON THE AREAS WHICH THE RELATED DEVICES ARE LOCATED. 9- TWO DOORS SHALL BE CONSIDERED FOR EACH FRONT AND REAR ACCESS. 10- THE TAG AND DESCRIPTION FOR ALL BUTTONS AND LAMPS SHALL BE PROVIDED. THE MATERIAL OF TAGS SHALL BE S.S. 10 CHARACTERS FOR TAGs AND 32 CHARACTERS FOR DESCRIPTION TO BE CONSIDERED AS A MINIMUM. 11- VENDOR SHALL PROVIDE SYMBOL & LEGEND FOR DEVICE USED IN ESD CONSOLE. THIS LEGEND & SYMBOL SHALL BE ADDED TO ALL PANEL LAYOUTS. 12- IF ANY ELECTRICAL EQUIPMENT, FAN AND OTHER DEVICES ARE REQUIRED IN THE ESD CONSOLE; SPARE SPACE SHALL BE CONSIDERED ON THE CONSOLE.
D03

## F&G MATRIX PANEL
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ESD CONSOLE/ F&G MATRIX PANEL
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 9
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | IN | DT | 0017 | D03
F&G MATRIX PANEL
| DIMENSION | [5 empty] | 120X75 cm2 (Refer to the Attachment)
| THICKNESS | [5 empty] | 3MM
| NUMBER OF BUTTONS FOR F&G MATRIX | [5 empty] | 4 PUSH BUTTON, + 9 MUSHROOM HEAD LATCH (LOCKABLE) P.B.
| NUMBER OF LAMPS FOR F&G MATRIX | [5 empty] | 48 (15 Red, 12 Blue, 12 Yellow, 9 Orange)
| LAMP COLOR FOR F&G MATRIX | [5 empty] | 15 RED, 12 BLUE, 12 YELLOW, 9 ORANGE
| BUTTON TYPE | [5 empty] | PUSH BUTTON (P.B.) , MUSHROOM HEAD LATCH P.B. with cover
| INGRESS PROTECTION | [5 empty] | IP54
| MATERIAL | [5 empty] | SHEET STEEL (According to manufacturer/supplier’s own standards)
| CONSOLE COLOR | [5 empty] | RAL 7035
| ACCESS | [5 empty] | FRONT and REAR (VTC)
| CABLE ENTRY | [5 empty] | FROM CONSOLE BOTTOM
| CONSOLE CONTENT | [5 empty] | ALARM ANNUNCIATE, PUSH BUTTONS, INDICATING LAMPS and N.I.S. I/O TERMINATION
| POWER RANGE | [5 empty] | 24 VDC
NOTES: 2- SUITABLE GLAND WITH SPARE PLUGGED CABLE ENTRIES TO BE CONSIDERED. 3- PUSH BUTTONS AND LAMPS SHALL BE CONSIDERED. 4- 20% SPARE BUTTONS AND LAMPS (NOT CONNECTED) SHALL BE CONSIDERED ON THE CONSOLE. 5- SPARE PARTS FOR COMMISSIONING AND 2 YEARS TO BE PROVIDED. 6- IN ORDER TO HAVE AUDIBLE ALARM HORN TO BE CONSIDERED . 7- IF ANY RELAY, BARRIER AND OTHER DEVICES ARE REQUIRED IN THE ESD CONSOLE, IT SHALL BE SIL3. 8- ARRANGMENT OF THE PUSHBUTTONS AND LAMPS SHALL BE BASED ON THE AREAS WHICH THE RELATED DEVICES ARE LOCATED. 9- TWO DOORS SHALL BE CONSIDERED FOR EACH FRONT AND REAR ACCESS. 10- THE TAG AND DESCRIPTION FOR ALL BUTTONS AND LAMPS SHALL BE PROVIDED. THE MATERIAL OF TAGS SHALL BE S.S. 10 CHARACTERS FOR TAGs AND 32 CHARACTERS FOR DESCRIPTION TO BE CONSIDERED AS A MINIMUM. 11- VENDOR SHALL PROVIDE SYMBOL & LEGEND FOR DEVICE USED IN ESD CONSOLE. THIS LEGEND & SYMBOL SHALL BE ADDED TO ALL PANEL LAYOUTS. 12- IF ANY ELECTRICAL EQUIPMENT, FAN AND OTHER DEVICES ARE REQUIRED IN THE F&G MATRIX; SPARE SPACE SHALL BE CONSIDERED ON THE PANEL. 13-ALL VISUAL ALARMS SHOULD DISTIGUISH BETWEEN PRE ALARM AND ALARM BY ASSINGING DIFFERENT FREQUENCY ON/OFF LAMP.
D03

## LEGEND
NISOC | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ESD CONSOLE/ F&G MATRIX PANEL
شماره پیمان: | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 | BK | GCS | PEDCO | 120 | IN | DT | 0017 | D03
D03

## ESD SCHEMATIC
NISOC | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ESD CONSOLE/ F&G MATRIX PANEL
شماره پیمان: | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 | BK | GCS | PEDCO | 120 | IN | DT | 0017 | D03
D03

## F&G SCHEMATIC
NISOC | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ESD CONSOLE/ F&G MATRIX PANEL
شماره پیمان: | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 | BK | GCS | PEDCO | 120 | IN | DT | 0017 | D03
D03

## DIMENSION ESTIMATE
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR ESD CONSOLE/ F&G MATRIX PANEL
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | IN | DT | 0017 | D03
Class: 1
D03