## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DG-0005 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2522 |  |  | Transmital Date: 12/26/2023
Document Title: Control System Loop Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-2522 |  |  | Transmital Date: 12/26/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-IN-DG-0005_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مدرک BK-GCS-PEDCO-120-IN-LI-0003 که در رفرنس عنوان شده مربوط به سیستم ESD می باشد. |  | 1402-2294-425937 | 1402/10/18 | اصلاح شد.
2 | به چه علت برای سیگنالهای دیجیتال هم از فیوز استفاده شده هم از نایف ترمینال؟ |  | 1402-2294-425937 | 1402/10/18 | عطف به مدرک SPECIFICATION FOR CONTROL SYSTEM: فیوز به علت جلوگیری از Over Current در سیگنالهای دیجیتال استفاده شده است: For Digital Signals: Each input point shall be individually protected against over-current. Each output shall be individually protected against over current. و علت استفاده از ترمینال چاقویی: - All terminals for field cables shall be "knife switch" type terminals.
3 | به چه علت برای برخی از ترانسمیترها بریر ریداندانت استفاده شده و برای برخی دیگر نه؟ مبنای این تمایز چیست؟ |  | 1402-2294-425937 | 1402/10/18 | عطف به آیتم 6.3.2 مدرک SPECIFICATION FOR CONTROL SYSTEM: • Analogue I/O used for control loop shall be redundant with hot-back-up • Digital I/O used for interlocks and control sequences shall be redundant with hot- back-up آیتم هایی که برای کنترل بکار رفته اند، Redundant در نظر گرفته شده اند. ترنسمیتر هایی که فقط مسئولیت نمایش دیتا را بر عهده دارند، single هستند.
4 | ریپلای شیت ارسالی برای این مدرک صحیح نمی باشد و مربوط به مدرکی دیگر است. بنابراین مدرک جهت اصلاح عودت داده می شود. |  | 1402-2294-425937 | 1402/10/18 | اصلاح شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: