## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DG-0005 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2522 |  |  | Transmital Date: 12/26/2023
Document Title: Control System Loop Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-2522 |  |  | Transmital Date: 12/26/2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-IN-DG-0005_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به بند 13 قرارداد و نوع مدرك مسئوليت تعداد و نوع تجهيزات به كار رفته از نظر مالي و زماني بر عهده پيمانكار (هيرگان) مي باشد. |  | BK-SUR-ENG-INS-01-05231 | 2022-07-25 | ملاحظه شد. |  |  | بسته شد
2 | با توجه به تغييرات ارائه شده در جلسه HAZOP/SIL/HAZID موارد مجددا بررسي و ارسال گردد. |  | BK-SUR-ENG-INS-01-05231 | 2022-07-25 | اصلاح شد. |  |  | بسته شد
D01 Replaced
1 | با توجه به نهایی نبودن پکیج ها، در صورت تغییر در این مدرک نیز در نظر گرفته شود. |  | BK-SUR-ENG-INS-02-08936 | 2024-01-10 | ملاحظه شد.
2 | نقطه نظرات بپیوست ارسال می گردد. |  | BK-SUR-ENG-INS-02-08936 | 2024-01-10 | اعمال شد.
3 | نقطه نظرات کارفرما بپیوست ارسال می گردد. |  | BK-SUR-ENG-INS-02-08936 | 2024-01-10 | اعمال شد.
4 | در خصوص استفاده همزمان از ترمینال چاقویی و فیوزی شفاف سازی گردد. |  | BK-SUR-ENG-INS-02-08936 | 2024-01-10 | عطف به مدرک SPECIFICATION FOR CONTROL SYSTEM: فیوز به علت جلوگیری از Over Current در سیگنالهای دیجیتال استفاده شده است: For Digital Signals: Each input point shall be individually protected against over-current. Each output shall be individually protected against over current. و علت استفاده از ترمینال چاقویی: - All terminals for field cables shall be "knife switch" type terminals.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: