## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-SP-0007 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1839 |  |  | Transmital Date: 2/1/2023
Document Title: Specification For Air Dryer Package |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-ME-TR-1839 |  |  | Transmital Date: 2/1/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-ME-SP-0007_D02 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | همانگونه که در نامه شماره 01/2294/325717 بیان شده است عبارت: Microprocessor حذف گردد تا امکان ارائه پیشنهاد های دیگر و بهتر برای سازندگان فراهم باشد. |  | 1402-2294-30925 | 1402/01/30 | مطابق نظر کارفرمای محترم اصلاح شد.
2 | توضیحات در خصوص خشک کننده های هوا با مجموعه کمپرسور های هوا به گونه ای اصلاح گردد که: اولا مشخص شود که کمپرسور هوا دارای UCP مختص خود می باشند. ثانیا خشک کنندهای هوا نیز دارای LCP مختص خود باشند. ثالثا هر کدام از خشک کنندها فارغ از اینکه کدام کمپرسور هوا در سرویس باشد بتواند کار کند. |  | 1402-2294-30925 | 1402/01/30 | مطابق نظر کارفرمای محترم اصلاح شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: