## Aghajari-1
ASIA INSTRUMENTS LTD. CO.
Factory: Mehrshahr-Eram BLVD
PAYAM Economic Special Zoon, Asia instruments Factory
Ph : (0098) 26-34 92 1581-2-5-6 (Ext.539)
Fax : (0098) 26-34 92 15 83
e-mail : info@asiainstrumentsltd.com
MAIL TO :
ATTN :
| Proposed By : M. Javadian |  | rev01
Date :20-May.-2024
| GENERAL DATA |  |  |  |  | FLUID DATA | [5 empty] | TRANSMITTER
| TAG NO. | LINE CLASS | NACE CERTIFICATE | SIL 2 CERTIFICATE | Lightning Protection | SERVICE. | STATE | OPER. PRESSURE (barg) | OPER. TEMP. (°C) | DESIGN PRESSURE Barg | DESIGN TEMP. (°C) | INSTRUMENT TYPE | XMTR. RANGE | Overpressure limits | INGRESS PROTECTION | ELEMENT TYPE | ELEMENT MATERIAL | ELEMENT FILL FLUID | PROCESS CONNECTION | MOUNTING | TYPE | RATING | PACKING MATERIAL | PROCESS CONNECTION | TRANSMITTER MODEL NO. | MANIFOLD MANUFACTURER | MODEL NO. | Syphons | Range Protection | scale layout | accuracy | movement | Window | standard
bsof
1 | PG-2101 | AN07 | Required | - | yes | EXISTING GAS PIG RECEIVER | Gas | 7.5 | 46.11/26.67 | 18.2 | 85 | Pressure gauge | 0 ~ 16barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.1
2 | PG-2102 | AN07 | Required | - | yes | EXISTING GAS PIG RECEIVER | Gas | 7.5 | 46.11/26.67 | 18.2 | 85 | Pressure gauge | 0 ~ 16barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.2
3 | PG-2103 | FN07 | Required | - | yes | GAS PIG RECEIVER | Gas | 7.5 | 15.5-32 | 175 | 85 | Pressure gauge | 0 ~ 16barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.3
4 | PG-2104 | FN07 | Required | Required | yes | GAS PIG RECEIVER | Gas | 7.5 | 15.5-32 | 175 | 85 | Pressure gauge | 0 ~ 16barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.4
5 | PG-2111 | AN07 | Required | Required | yes | SLUG CATCHER DRUM | Gas | 5.5 | 15.5-32 | FV/9 | 85 | Pressure gauge | 0 ~ 10barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.5
6 | PG-2114A | AS00 | Required | - | yes | SLUG PUMPS | LIQUID | 5.5 | 23.22/8.82 | 13.9 | 85 | Pressure gauge | 0 ~ 10barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.6
7 | PG-2113A | CN05 | Required | - | yes | SLUG PUMPS | LIQUID | 19.5 | AMB | 47.7 | 85 | Pressure gauge | 0 ~ 40barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.7
8 | PG-2113B | CN05 | Required | - | yes | SLUG PUMPS | LIQUID | 19.5 | AMB | 47.7 | 85 | Pressure gauge | 0 ~ 40barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.8
9 | PG-2114B | AS00 | Required | - | yes | SLUG PUMPS | LIQUID | 5.5 | 23.22/8.82 | 13.9 | 85 | Pressure gauge | 0 ~ 10barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.9
10 | PG-2114 | AN07 | Required | - | yes | INLET KNOCK OUT DRUM | Gas | 5.3 | 19-37 | FV/9 | 85 | Pressure gauge | 0 ~ 10barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.10
11 | PG-2115 | AN07 | Required | - | yes | GAS | Gas | 5.1 | 19-37 | 18.2 | 85 | Pressure gauge | 0 ~ 10barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.11
12 | PG-2121A | CN05 | Required | Required | yes | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #A | Gas | 5.1 | 19-37 | FV/22 | 85 | Pressure gauge | 0 ~ 10barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.12
13 | PG-2121B | CN05 | Required | Required | yes | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #B | Gas | 5.1 | 19-37 | FV/23 | 85 | Pressure gauge | 0 ~ 10barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.13
14 | PG-2121C | CN05 | Required | - | yes | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #C | Gas | 5.1 | 19-37 | FV/24 | 85 | Pressure gauge | 0 ~ 10barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.14
15 | PG-2122A | CN05 | Required | - | yes | 1ST STAGE GAS COMPRESSOR TRAIN#A | Gas | 4.9 | 18-35 | 47.7 | 85 | Pressure gauge | 0 ~ 10barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.15
16 | PG-2123A | CN05 | Required | - | yes | 1ST STAGE GAS COMPRESSOR TRAIN#A | Gas | 19 | 113/124 | 47.7 | 155 | Pressure gauge | 0 ~ 40barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.16
17 | PG-2122B | CN05 | Required | - | yes | 1ST STAGE GAS COMPRESSOR TRAIN#B | Gas | 4.9 | 18-35 | 47.7 | 85 | Pressure gauge | 0 ~ 10barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.17
18 | PG-2123B | CN05 | Required | - | yes | 1ST STAGE GAS COMPRESSOR TRAIN#B | Gas | 19 | 113/124 | 47.7 | 155 | Pressure gauge | 0 ~ 40barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.18
19 | PG-2122C | CN05 | Required | Required | yes | 1ST STAGE GAS COMPRESSOR TRAIN#C | Gas | 4.9 | 18-35 | 47.7 | 85 | Pressure gauge | 0 ~ 10barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.19
20 | PG-2123C | CN05 | Required | Required | yes | 1ST STAGE GAS COMPRESSOR TRAIN#C | Gas | 19 | 113/124 | 47.7 | 155 | Pressure gauge | 0 ~ 40barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.20
21 | PG-2124A | CN05 | Required | - | yes | 1ST STAGE GAS COMPRESSION AIR COOLER TRAIN #A | Two Phase (Gas+Liq) | 18.3 | 60 | 30.3 | 155 | Pressure gauge | 0 ~ 40barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.21
22 | PG-2124B | CS00 | Required | - | yes | 1ST STAGE GAS COMPRESSION AIR COOLER TRAIN #B | Two Phase (Gas+Liq) | 18.3 | 60 | 30.3 | 155 | Pressure gauge | 0 ~ 40barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.22
23 | PG-2124C | CS00 | Required | - | yes | 1ST STAGE GAS COMPRESSION AIR COOLER TRAIN #C | Two Phase (Gas+Liq) | 18.3 | 60 | 30.3 | 155 | Pressure gauge | 0 ~ 40barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.23
24 | PG-2131A | CS00 | Required | Required | yes | 2ND STAGE GAS COMPRESSOR CUCTION DRUM TRAIN #A | Gas | 18.3 | 60 | FV/22 | 115.4 | Pressure gauge | 0 ~ 40barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.24
25 | PG-2131B | CS00 | Required | - | yes | 2ND STAGE GAS COMPRESSOR CUCTION DRUM TRAIN #B | Gas | 18.3 | 60 | FV/23 | 115.4 | Pressure gauge | 0 ~ 40barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.25
26 | PG-2131C | CS00 | Required | - | yes | 2ND STAGE GAS COMPRESSOR CUCTION DRUM TRAIN #C | Gas | 18.3 | 60 | FV/24 | 115.4 | Pressure gauge | 0 ~ 40barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.26
27 | PG-2132A | CS00 | Required | Required | yes | 2ND STAGE GAS COMPRESSOR TRAIN#A | Gas | 18.1 | 59-60 | 47.7 | 115.4 | Pressure gauge | 0 ~ 40barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.27
28 | PG-2133A | CN05 | Required | - | yes | 2ND STAGE GAS COMPRESSOR TRAIN#A | Gas | 54.8 | 142-150 | 90 | 175 | Pressure gauge | 0 ~100barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.28
29 | PG-2132B | FN05 | Required | Required | yes | 2ND STAGE GAS COMPRESSOR TRAIN#B | Gas | 18.1 | 59-60 | 47.7 | 115.4 | Pressure gauge | 0 ~40barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.29
30 | PG-2133B | CN05 | Required | Required | yes | 2ND STAGE GAS COMPRESSOR TRAIN#B | Gas | 54.8 | 142-150 | 90 | 175 | Pressure gauge | 0 ~100barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.30
31 | PG-2132C | FN05 | Required | Required | yes | 2ND STAGE GAS COMPRESSOR TRAIN#C | Gas | 18.1 | 59-60 | 47.7 | 115.4 | Pressure gauge | 0 ~40barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.31
32 | PG-2133C | CN05 | Required | Required | yes | 2ND STAGE GAS COMPRESSOR TRAIN#C | Gas | 54.8 | 142-150 | 90 | 175 | Pressure gauge | 0 ~100barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.32
33 | PG-2134A | FN05 | Required | - | yes | 2ND STAGE GAS COMPRESSION AIR COOLER TRAIN#A | Two Phase (Gas+Liq) | 54.1 | 60 | 62.4 | 175 | Pressure gauge | 0 ~100barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.33
34 | PG-2134B | FS00 | Required | - | yes | 2ND STAGE GAS COMPRESSION AIR COOLER TRAIN#B | Two Phase (Gas+Liq) | 54.1 | 60 | 62.4 | 175 | Pressure gauge | 0 ~100barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.34
35 | PG-2134C | FS00 | Required | Required | yes | 2ND STAGE GAS COMPRESSION AIR COOLER TRAIN#C | Gas | 54.1 | 60 | 62.4 | 175 | Pressure gauge | 0 ~100barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.35
36 | PG-2142 | FS00 | Required | - | yes | GAS COMPRESSION DISCHARGE DRUM | Gas | 53.9 | 59-60 | 90 | 130 | Pressure gauge | 0 ~100barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.36
37 | PG-2141 | FN05 | Required | Required | yes | GAS COMPRESSION DISCHARGE DRUM | LIQUID | 53.9 | 59-61 | FV/62 | 130 | Pressure gauge | 0 ~100barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | YES | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.37
38 | PG-2162 | FN05 | - | Required | yes | GLYCOL TRANSFER PUMP | LIQUID | 0.02 | AMB | 18.2 | 85 | Pressure gauge | 0-40 mbar | 1.3 x full scale value | IP65 | Diaphragm | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 432.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.38
39 | PG-2163A | AN04 | - | - | yes | GLYCOL TRANSFER PUMP | LIQUID | 2.1 | AMB | 18.2 | 85 | Pressure gauge | 0 ~4barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.39
40 | PG-2163B | AN04 | - | Required | yes | GLYCOL TRANSFER PUMP | Gas | 2.1 | AMB | 18.2 | 85 | Pressure gauge | 0 ~4barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.40
41 | PG-2161 | AN04 | Required | Required | yes | LEAN GLYCOL STORAGE TANK | Gas | 0.1 | AMB | 160MBARG/-7MBARG | 85 | Pressure gauge | 0-40 mbar | 1.3 x full scale value | IP65 | Diaphragm | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 432.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.41
42 | PG-2298 | AN07 | - | - | yes | LEAN GLYCOL STORAGE TANK | Gas | 0.1 | AMB | 18.2 | 85 | Pressure gauge | 0-40 mbar | 1.3 x full scale value | IP65 | Diaphragm | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 432.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.42
43 | PG-2201 | AN04 | - | Required | yes | Instrument Air Receiver | Gas | 8 | 65 | 18.2 | 85 | Pressure gauge | 0 ~ 16 barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.43
44 | PG-2202 | AZ00 | - | Required | yes | Instrument Air Receiver | Gas | 8 | 65 | 12.5 | 85 | Pressure gauge | 0 ~ 16 barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.44
45 | PG-2211 | AZ00 | - | - | yes | Nitrogen Reveiver | Gas | 8 | 60 | 18.2 | 85 | Pressure gauge | 0 ~ 16 barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.45
46 | PG-2212 | AN01 | - | Required | yes | Nitrogen Reveiver | LIQUID | 8 | 60 | 12.5 | 85 | Pressure gauge | 0 ~ 16 barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.46
47 | PG-2221 | AN01 | Required | Required | yes | closed drain drum | LIQUID | 0.5 | AMB | FV/6.0 | 85 | Pressure gauge | 0 ~ 1 barg | 1.3 x full scale value | IP65 | Diaphragm | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 432.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.47
48 | PG-2232A | AN07 | Required | - | yes | closed drain drum | LIQUID | 7 | AMB | 18.2 | 85 | Pressure gauge | 0 ~ 16 barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.48
49 | PG-2232B | AN07 | Required | Required | yes | closed drain drum | LIQUID | 7 | AMB | 18.2 | 85 | Pressure gauge | 0 ~ 16 barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.49
50 | PG-2222A | AN07 | - | Required | yes | closed drain drum | LIQUID | 2 | AMB | 18.2 | 85 | Pressure gauge | 0 ~ 4 barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.50
51 | PG-2222B | AN01 | - | Required | yes | closed drain drum | Gas | 2 | AMB | 18.2 | 85 | Pressure gauge | 0 ~ 4 barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.51
52 | PG-2251 | AN01 | Required | Required | yes | LP flare K.O.drum | LIQUID | 0.5 | 32 | FV/6.0 | 85 | Pressure gauge | 0 ~ 1 barg | 1.3 x full scale value | IP65 | Diaphragm | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 432.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.52
53 | PG-2251A | AN07 | Required | Required | yes | LP flare K.O.drum pump | LIQUID | 1.6 | AMB | 18.2 | 85 | Pressure gauge | 0 ~ 4 barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.53
54 | PG-2251B | AN07 | Required | Required | yes | LP flare K.O.drum pump | Gas | 1.6 | AMB | 18.2 | 85 | Pressure gauge | 0 ~ 4 barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.54
55 | PG-2272 | AN07 | Required | Required | yes | FUEL GAS | Gas | 5.1 | 19-37 | 18.2 | 85 | Pressure gauge | 0 ~ 10barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.55
56 | PG-2273 | AN07 | Required | - | yes | FUEL GAS | Gas | 4.9 | 19-37 | FV/9 | 85 | Pressure gauge | 0 ~ 10barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.56
57 | PG-2271 | AN07 | Required | Required | yes | FUEL GAS | Gas | 4.9 | 33.6 | 18.2 | 85 | Pressure gauge | 0 ~ 10barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.57
58 | PG-2274 | AN07 | Required | Required | yes | FUEL GAS | LIQUID/OIL | 0.5 | 33.6 | 18.2 | 85 | Pressure gauge | 0 ~ 1barg | 1.3 x full scale value | IP65 | Diaphragm | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 6000# | PTFE | 1/2" NPTF | 432.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.58
59 | PG-2282 | AN07 | - | - | yes | OIL | LIQUID/OIL | 0.95 | 5-50 | 18.2 | 85 | Pressure gauge | 0 ~ 2.5barg | 1.3 x full scale value | IP65 | Diaphragm | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 432.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.59
60 | PG-2283 | AN01 | - | Required | yes | OIL | LIQUID | 0.95 | 5-50 | 18.2 | 85 | Pressure gauge | 0 ~ 2.5barg | 1.3 x full scale value | IP65 | Diaphragm | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 432.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.60
61 | PG-2291 | AN01 | - | Required | yes | Potable Water | LIQUID | 1.95 | AMB | 18.2 | 85 | Pressure gauge | 0 ~ 4barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.61
62 | PG-2292 | AZ00 | - | Required | yes | Potable Water | LIQUID | 0.15 | AMB | 18.2 | 85 | Pressure gauge | 0-250 mbar | 1.3 x full scale value | IP65 | Diaphragm | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 432.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.62
63 | PG-2293 | AZ00 | - | - | yes | RICH GLYCOL | LIQUID | 2.1 | AMB | 18.2 | 85 | Pressure gauge | 0 ~ 4barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.63
64 | PG-2294 | AN04 | - | Required | yes | Right Glycol | Gas | 0.01 | AMB | FV/3.5 | 85 | Pressure gauge | 0-250 mbar | 1.3 x full scale value | IP65 | Diaphragm | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 432.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.64
65 | PG-2295 | AN04 | - | - | yes | GLYCOL SUMP DRUM | LIQUID | 0.5 | AMB | 18.2 | 85 | Pressure gauge | 0 ~ 1barg | 1.3 x full scale value | IP65 | Diaphragm | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 432.30 | WIKA | IV20 | NO | YES | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.65
66 | PG-2301 | AN04 | - | Required | yes | Fire Water | LIQUID | 11.3 | AMB | 17 | 85 | Pressure gauge | 0 ~ 25barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.66
67 | PG-2305 | AN04 | - | Required | yes | Fire Water | LIQUID | 11.3 | AMB | 17 | 85 | Pressure gauge | 0 ~ 25barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.67
68 | PG-2303A | AN04 | - | - | yes | Fire Water | LIQUID | 1 | AMB | 1.5 | 85 | Pressure gauge | 0 ~ 2.5barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.68
69 | PG-2304A | AN04 | - | Required | yes | Fire Water | LIQUID | 11.3 | AMB | 17 | 85 | Pressure gauge | 0 ~ 25barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.69
70 | PG-2303B | AN04 | - | Required | yes | Fire Water | LIQUID | 1 | AMB | 1.5 | 85 | Pressure gauge | 0 ~ 2.5barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.70
71 | PG-2304B | AN04 | - | - | yes | Fire Water | LIQUID | 11.3 | AMB | 17 | 85 | Pressure gauge | 0 ~ 25barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.71
72 | PG-2304 | AN04 | - | Required | yes | Fire Water | LIQUID | 11 | AMB | 16.5 | 85 | Pressure gauge | 0 ~ 25barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.72
73 | PG-2301A | AN04 | - | Required | yes | Fire Water | LIQUID | 1 | AMB | 1.5 | 85 | Pressure gauge | 0 ~ 2.5barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.73
74 | PG-2302A | AN04 | - | - | yes | Fire Water | LIQUID | 11.3 | AMB | 17 | 85 | Pressure gauge | 0 ~ 25barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.74
75 | PG-2301B | AN04 | - | Required | yes | Fire Water | LIQUID | 1 | AMB | 1.5 | 85 | Pressure gauge | 0 ~ 2.5barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.75
76 | PG-2302B | AN04 | - | Required | yes | Fire Water | LIQUID | 11.3 | AMB | 17 | 85 | Pressure gauge | 0 ~ 25barg | 1.3 x full scale value | IP65 | Bourdon | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 2-VALVE | 3000# | PTFE | 1/2" NPTF | 233.30 | WIKA | IV20 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | Stainless steel | Laminated safety glass | ANSI / ASME B1.20.76
| TAG NO. | LINE CLASS | NACE CERTIFICATE | SIL 2 CERTIFICATE | Lightning Protection | SERVICE. | STATE | perating Pressure (barg) / Differential Pressure (bar | OPER. TEMP. (°C) | DESIGN PRESSURE Barg | DESIGN TEMP. (°C) | INSTRUMENT TYPE | XMTR. RANGE | Overpressure limits | INGRESS PROTECTION | ELEMENT TYPE | ELEMENT MATERIAL | ELEMENT FILL FLUID | PROCESS CONNECTION | MOUNTING | TYPE | RATING | PACKING MATERIAL | PROCESS CONNECTION | TRANSMITTER MODEL NO. | MANIFOLD MANUFACTURER | MODEL NO. | Syphons | Range Protection | scale layout | accuracy | movement | Window | standard
1 | PDG-2114A | AS00 | Required |  |  | BEFORE SLUG PUMP A | LIQUID | 5.5 / 1.5 | 23.22/8.82 | 13.9 | 85 | DIFFERENTIAL PRESSURE GAUGE | 0 ~ 2.5barg | - | IP65 | DIAPHRAGM | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 5-VALVE |  | PTFE | 1/2" NPTF | 733.31 | WIKA | IV504 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | The accuracy is ±1%. | Laminated safety glass | ANSI / ASME B1.20.75
2 | PDG-2114B | AS00 | Required |  |  | BEFORE SLUG PUMP B | LIQUID | 5.5 / 1.5 | 23.22/8.82 | 13.9 | 85 | DIFFERENTIAL PRESSURE GAUGE | 0 ~ 2.5barg | - | IP66 | DIAPHRAGM | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 5-VALVE |  | PTFE | 1/2" NPTF | 733.31 | WIKA | IV505 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | The accuracy is ±1%. | Laminated safety glass | ANSI / ASME B1.20.76
3 | PDG-2271 | - | Required |  |  | FUEL GAS K.O. DRUM | GAS | 4.9 / 1.5 | 33.6 | FV/9 | 85 | DIFFERENTIAL PRESSURE GAUGE | 0 ~ 2.5barg | - | IP67 | DIAPHRAGM | S.S 316 L | Silicone Oil | 1/2" NPT | Manifold Support | 5-VALVE |  | PTFE | 1/2" NPTF | 733.31 | WIKA | IV506 | NO | NO | dual scale as per data sheet | The accuracy is ±1%. | The accuracy is ±1%. | Laminated safety glass | ANSI / ASME B1.20.77
| commissioning spare part | DESCRIPTION | QTY. |  |  |  | 2YEARS SPARE PART | DESCRIPTION | QTY.
|  | Similar to tag PG-2111 | 1 |  |  |  |  | Similar to tag PG-2111 | 1
|  | Similar to tag PG-2101 | 1 |  |  |  |  | Similar to tag PG-2101 | 1
|  | Similar to tag PG-2303A | 1 |  |  |  |  | Similar to tag PG-2303A | 1
|  | Similar to tag PG-2301 | 1 |  |  |  |  | Similar to tag PG-2301 | 1
|  | Similar to tag PG-2163A | 1 |  |  |  |  | Similar to tag PG-2163A | 1
|  | Similar to tag PG-2113A | 1 |  |  |  |  | Similar to tag PG-2113A | 1
|  | Similar to tag PG-2133A | 1 |  |  |  |  | Similar to tag PG-2133A | 1
|  | DESCRIPTION | QTY. |  |  |  |  | DESCRIPTION | QTY.
|  | Similar to tag PG-2221 | 1 |  |  |  |  | Similar to tag PG-2221 | 1
|  | Similar to tag PG-2281 | 1 |  |  |  |  | Similar to tag PG-2281 | 1
|  | Similar to tag PG-2292 | 1 |  |  |  |  | Similar to tag PG-2292 | 1
|  | Similar to tag PG-2162 | 1 |  |  |  |  | Similar to tag PG-2162 | 1
|  | Similar to tagPDG-2114A | 1 |  |  |  |  | Similar to tagPDG-2114A | 1