## Sheet1
Requisition Reference Title : نگهداشت و افزایشتولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوري بینک
vendor Name: Sangan sanat |  | Deviation List |  | Date: 19-May-2024
|  | Requisition Reference No.: BK-GCS-PEDCO-120-IN-MR-0010_D01 |  | Rev:01
No. | Document No. & Clause No. | Project Requirement | Vendor replay | Acceptance / Rejection by PURCHASER
1 | Datasheet of differential pressure gauge ITEM 25 | Accuracy is ±0.5% of F.S. | 2-Accuracy for differential pressure gauge is 1.6% F.S.D (In operational conditions, accuracy cannot be better than this. Otherwise, it is Better to use DP transmitter. Please refer to Deviation list
2 | Datasheet of pressure gauge TAGs: PG-2221 PG-2251 PG-2274 PG-2282 PG-2283 PG-2295 | element type is Diaphragm | for pressure range higher than 0.6 bar , bordun tube is used
3 | Datasheet of pressure gauge TAGs: PG-2162 PG-2161 PG-2298 PG-2292 PG-2294 | Case is Liquid. Filled | for pressure gauge lower than 0.6 bar (diaphragm type) , Case cannot be filled.
4 | 4- GCS_TCL for PG-D00 - Sangan Sanat item 28 | Diaphragm gauges shall also be solid front acc. to project data sheet | Diaphragm & capsule pressure gauge is not solid front (safety is S2) Note: Solid Front gauge is used to protect against high pressures.
5 | 4- GCS_TCL for PG-D00 - Sangan Sanat item 34 | Regarding differential pressure gauge, these devices shall also be safety pattern type. | Differential pressure gauge diaphragm type is not solid front (safety is S2) Note: Solid Front gauge is used to protect against high pressures.
6