## TBE for TG
'نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE For Temperature Gauge
|  |  | Project Code |  | Package | Company code |  | Scope | Disc Code | Doc. Code | Sequence No. | Rev. Code
|  |  | BK |  | GCS | PEDCO |  | 120 | IN | TB | 0013 | D00
REQ. NAME : |  | PMR for Temperature Gauge |  | BIDDER: Asia instrumet LTD.CO
REQ. NO. : |  | BK-GCS-PEDCO-120-IN-TB-0013 |  | NAME: M.JAVADIAN
REQ. REV. : |  | D03 |  | QUOTATION NO.:03-22743
EQUIPMENT TYPE : |  | Temperature Gauge |  | QUOTATION DATE: 2024/24/04
NO. | DESCRIPTION |  |  | REFERENCE / SPECIFIED
A | Scope of Work And Supply
1 | Tag Number
2 | Scope of Work And Supply |  |  | Temperature Gauge |  |  | A
3 | Delivary Date |  |  | B.V. |  |  | 5 months after PO
4 | Delivary Place |  |  | Ex.Work |  |  | A
5 | Bid Validity Period |  |  | B.V. |  |  | 1 month after quotation
6 | GUARANTEE |  |  | Requisition eighteen (18) months from the date of the Installation and Commissioning or twenty-four (24) months after the date of delivery of materials (whichever comes earlier) |  |  | A
7 | MANUFACTURER (VENDOR LIST) |  |  | AVL |  |  | A(WIKA)
8 | SPARE PARTS |  |  | 5% complete set (at least 1 set per type) |  |  | A
B | Technical Requirements
1 | Environmental / Process Condition |  |  | According to data sheet |  |  | A
2 | Thermometer Type |  |  | Bimetal / Filled type (As requested) |  |  | A
3 | Calibrated Range |  |  | As requested |  |  | A
4 | Dial Size |  |  | 150 mm |  |  | N/A(160mm)
5 | Dial Color |  |  | White with black Letter |  |  | A
6 | Case Material |  |  | Stainless Steel 304 |  |  | A
7 | Process Connection Size/ rating |  |  | 1 1/2 RTJ,/ API 3000 |  |  | as per data sheet process connection is 1 1/2 RF
8 | Eng. Unit |  |  | °C/ °F |  |  | A
9 | Accuracy |  |  | Better than ± 1% of full span |  |  | A
10 | Pointer Color / Material |  |  | Black / Metallic |  |  | A
11 | Stem Type / Material |  |  | Threaded / 316 SS |  |  | A
12 | Stem Diameter |  |  | 6 mm |  |  | A
13 | Ingress Protection |  |  | IP65 |  |  | A
14 | Window Material |  |  | Shatterproof Glass |  |  | A
15 | Zero Adjustment |  |  | Pointer |  |  | A
16 | Over range Protection |  |  | 1.5 times the maximum scale. |  |  | A
17 | Connection |  |  | Every Angle |  |  | A
18 | External Calibration Adjustment |  |  | Required |  |  | A
19 | Head Type |  |  | Oriantable Head |  |  | A
20 | Thermowell |  |  | Tapered Drilled Bar Stock |  |  | A
21 | Well conn. & Flange Material |  |  | As requested & Stainless Steel 316 |  |  | A
22 | Thermowell Connection to thermometer |  |  | 1/2" NPTF |  |  | A
23 | In Complaince with Nace Standard |  |  | As requested |  |  | A
24 | Insertion Length (U) mm |  |  | As requested |  |  | A
25 | SS Name Plate |  |  | As requested |  |  | A
26 | Accessories for installation for remote type |  |  | As requested |  |  | A
C | Test and Inspection
1 | Test and Inspection |  |  | Project IDS, Requisition |  |  | A
D | Document Requirements
1 | Country Of Origin |  |  | Contract |  |  | A
2 | Wake Frequency Calculaton |  |  | Requisition |  |  | A(After PO)
3 | Material Test / Calibration Certificate |  |  | Requisition |  |  | A
4 | Level of Similar Experience in past 10 years |  |  | Vendor 's Quotation |  |  | A(Refer to refrence list)
F | Deviations / Alternatives
1 | Deviations (if any) |  |  | signed and stamped |  |  | A
2 | Manufacturer's Location | [5 empty] | Payam Special Economic Zone, Mehrshahr, Alborz,Iran
H | PROPOSAL DOCUMENTATION
1 | Quality plan / ITP |  |  | shall be submitted |  |  | A
2 | Standard certificates |  |  | shall be submitted |  |  | A
3 | Filled TBE |  |  | shall be submitted |  |  | A
4 | Summary sheets |  |  | shall be submitted |  |  | A
5 | Subvendor list (if any) |  |  | shall be submitted |  |  | A
6 | Reference list |  |  | shall be submitted |  |  | A
7 | Catalouges |  |  | shall be submitted |  |  | A
8 | Datasheet/ Drawing |  |  | shall be submitted |  |  | A
9 | Order code (Part No.) |  |  | shall be submitted |  |  | A
GENERAL ACCEPTANCE FOR QUOTATION:
Notes:
A : ACCEPTABLE (TECHNICALLY MEETS REQUIREMENT)
NA: NOT ACCEPTABLE (TECHNICALLY DOES NOT MEET REQUIREMENT)
CA: CONDITIONALLY ACCEPTED
INA: INFORMATION NOT AVAILABLE
N/A: NOT APPLICABLE