## Aghajari-1
ASIA INSTRUMENTS LTD. CO.
Factory: Mehrshahr-Eram BLVD
PAYAM Economic Special Zoon, Asia instruments Factory
Ph : (0098) 26-34 92 1581-2-5-6 (Ext.539)
Fax : (0098) 26-34 92 15 83
e-mail : info@asiainstrumentsltd.com
MAIL TO :
ATTN :
| Proposed By : M. Javadian |  | rev01
Date :21-May.-2024
| GENERAL DATA |  |  | FLUID DATA | [5 empty] | TRANSMITTER
| TAG NO. | LINE CLASS | NACE CERTIFICATE | SERVICE. | STATE | OPER. PRESSURE (barg) | OPER. TEMP. (°C) | DESIGN PRESSURE Barg | DESIGN TEMP. (°C) | INSTRUMENT TYPE | Instrument Range (°C) | scale range | Overpressure limits | INGRESS PROTECTION | ELEMENT FILL FLUID | Process Connection Size(in) | MOUNTING | TYPE | RATING | PACKING MATERIAL | INSTRUMRNT PROCESS CONNECTION | TRANSMITTER MODEL NO. | Thermowell with flange Model TW10 | Connection location | DIAL SIZE (mm) | scale layout | flange material | Thermowell material wetted | accuracy | wetted material | Case, bayonet ring | Articulated joint (“adjustable stem and dial”) | Window | standard
bsof
1 | TG-2111 | AN07 | Required | SLUG CATCHER DRUM | Gas | 5.5 | 15.5-32 | FV/9 | 85 | TEMPERATURE GAUGE | 0-100 | -20-+120 | 100 % overload safety of scale range | IP65 | Silicone Oil | 2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
2 | TG-2112A | CN05 | Required | SLUG PUMP P-2101A DISCHARGE LINE | LIQUID | 19.5 | AMB | 47.7 | 85 | TEMPERATURE GAUGE | 0-100 | -20-+120 | 100 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
3 | TG-2112B | CN05 | Required | SLUG PUMP P-2101B DISCHARGE LINE | LIQUID | 19.5 | AMB | 47.7 | 85 | TEMPERATURE GAUGE | 0-100 | -20-+120 | 100 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
4 | TG-2113 | - | Required | INLET KNOCK OUT DRUM | Gas | 5.3 | 19-37 | FV/9 | 85 | TEMPERATURE GAUGE | 0-100 | -20-+120 | 100 % overload safety of scale range | IP65 | Silicone Oil | 2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
5 | TG-2114 | AN07 | Required | 1ST STAGE GAS COMPRESSION SUCTION MANIFOLD | Gas | 5.3 | 19-37 | 18.2 | 85 | TEMPERATURE GAUGE | 0-100 | -20-+120 | 100 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
6 | TG-2121A | - | Required | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #A | Gas | 5.1 | 19-37 | FV/22 | 85 | TEMPERATURE GAUGE | 0-100 | -20-+120 | 100 % overload safety of scale range | IP65 | Silicone Oil | 2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
7 | TG-2121B | - | Required | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #B | Gas | 5.1 | 19-37 | FV/22 | 85 | TEMPERATURE GAUGE | 0-100 | -20-+120 | 100 % overload safety of scale range | IP65 | Silicone Oil | 2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
8 | TG-2121C | - | Required | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #C | Gas | 5.1 | 19-37 | FV/22 | 85 | TEMPERATURE GAUGE | 0-100 | -20-+120 | 100 % overload safety of scale range | IP65 | Silicone Oil | 2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
9 | TG-2122A | AN05 | Required | FROM 1ST STAGE GAS COMP. SUCTION DRUM (V-2101A) TO C-2101-A | Gas | 4.9 | 18-35 | 47.7 | 85 | TEMPERATURE GAUGE | 0-100 | -20-+120 | 100 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
10 | TG-2123A | CN05 | Required | OUTLET COMP. C-2101-A / TO 1ST STAGE AIR COOLER (AE-2101A) | Gas | 19 | 113/125 | 47.7 | 155 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
11 | TG-2122B | AN05 | Required | FROM 1ST STAGE GAS COMP. SUCTION DRUM (V-2101B) TO C-2101-B | Gas | 4.9 | 18-35 | 47.7 | 85 | TEMPERATURE GAUGE | 0-100 | -20-+120 | 100 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
12 | TG-2123B | CN05 | Required | OUTLET COMP. C-2101-B / TO 1ST STAGE AIR COOLER (AE-2101B) | Gas | 19 | 113/125 | 47.7 | 155 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
13 | TG-2122C | AN05 | Required | FROM 1ST STAGE GAS COMP. SUCTION DRUM (V-2101C) TO C-2101-C | Gas | 4.9 | 18-35 | 47.7 | 85 | TEMPERATURE GAUGE | 0-100 | -20-+120 | 100 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
14 | TG-2123C | CN05 | Required | OUTLET COMP. C-2101-C / TO 1ST STAGE AIR COOLER (AE-2101C) | Gas | 19 | 113/125 | 47.7 | 155 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
15 | TG-2124A | CS00 | - | FROM 1ST STAGE GAS COMPRESSOR AIR COOLERS (AE-2101-A) | Gas/LIQUID | 18.3 | 60 | 30.3 | 155 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316 | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 304SS | Stainless steel | Laminated safety glass | EN 13190
16 | TG-2124B | CS00 | - | FROM 1ST STAGE GAS COMPRESSOR AIR COOLERS (AE-2101-B) | Gas/LIQUID | 18.3 | 60 | 30.3 | 155 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316 | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 304SS | Stainless steel | Laminated safety glass | EN 13190
17 | TG-2124C | CS00 | - | FROM 1ST STAGE GAS COMPRESSOR AIR COOLERS (AE-2101-C) | Gas/LIQUID | 18.3 | 60 | 30.3 | 155 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316 | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 304SS | Stainless steel | Laminated safety glass | EN 13190
18 | TG-2131A | - | Required | 2ND STAGE GAS COMPRESSOR SUCTION DRUM TRAIN #A | Gas | 18.3 | 60 | FV/22 | 115.4 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
19 | TG-2131B | - | Required | 2ND STAGE GAS COMPRESSOR SUCTION DRUM TRAIN #B | Gas | 18.3 | 60 | FV/22 | 115.4 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
20 | TG-2131C | - | Required | 2ND STAGE GAS COMPRESSOR SUCTION DRUM TRAIN #C | Gas | 18.3 | 60 | FV/22 | 115.4 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
21 | TG-2132A | CN05 | Required | 2ND STAGE GAS COMPRESSOR TRAIN #A SUCTION LINE | Gas | 18.1 | 59-60 | 47.7 | 115.4 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
22 | TG-2133A | FN05 | Required | 2ND STAGE GAS COMPRESSOR TRAIN #A DISCHARGE LINE | Gas | 54.8 | 142-150 | 90 | 175 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 600# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
23 | TG-2132B | CN05 | Required | 2ND STAGE GAS COMPRESSOR TRAIN #B SUCTION LINE | Gas | 18.1 | 59-60 | 47.7 | 115.4 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
24 | TG-2133B | FN05 | Required | 2ND STAGE GAS COMPRESSOR TRAIN #B DISCHARGE LINE | Gas | 54.8 | 142-150 | 90 | 175 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 600# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
25 | TG-2132C | CN05 | Required | 2ND STAGE GAS COMPRESSOR TRAIN #C SUCTION LINE | Gas | 18.1 | 59-60 | 47.7 | 115.4 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
26 | TG-2133C | FN05 | Required | 2ND STAGE GAS COMPRESSOR TRAIN #C DISCHARGE LINE | Gas | 54.8 | 142-150 | 9 | 175 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 600# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
27 | TG-2134A | FS00 | - | AE-2102A 2ND STAGE GAS COMPRESSION AIR COOLER TRAIN #A OUTLET | Gas/LIQUID | 54.1 | 60 | 62.4 | 175 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 600# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316 | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 304SS | Stainless steel | Laminated safety glass | EN 13190
28 | TG-2134B | FS00 | - | AE-2102B 2ND STAGE GAS COMPRESSION AIR COOLER TRAIN #B OUTLET | Gas/LIQUID | 54.1 | 60 | 62.4 | 175 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 600# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316 | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 304SS | Stainless steel | Laminated safety glass | EN 13190
29 | TG-2134C | FS00 | - | AE-2102C 2ND STAGE GAS COMPRESSION AIR COOLER TRAIN #C OUTLET | Gas/LIQUID | 54.1 | 60 | 62.4 | 175 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 600# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316 | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 304SS | Stainless steel | Laminated safety glass | EN 13190
30 | TG-2142 | FN05 | Required | GAS COMPRESSION DISCHARGE DRUM | GAS | 53.9 | 59-60 | 90 | 130 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 600# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
31 | TG-2141 | - | Required | GAS COMPRESSION DISCHARGE DRUM | Gas/LIQUID | 53.9 | 59-60 | FV/62 | 130 | TEMPERATURE GAUGE | 0-250 | -50- 300 | 50 % overload safety of scale range | IP65 | Silicone Oil | 2" | Manifold Support | 2-VALVE | 600# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
32 | TG-2161 | AN04 | - | LEAN GLYCOL STORAGE TANK TO DEHYDRATION PACKAGE | LIQUID | 2.1 | 30 | 18.2 | 85 | TEMPERATURE GAUGE | 0-100 | -20-+120 | 100 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316 | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 304SS | Stainless steel | Laminated safety glass | EN 13190
33 | TG-2221 | AN07 | Required | CLOSED DRAIN DRUM | LIQUID | 0.5 | AMB | FV/62 | 85 | TEMPERATURE GAUGE | 0-100 | -20-+120 | 100 % overload safety of scale range | IP65 | Silicone Oil | 1 1/2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
34 | TG-2251 | - | Required | LP FLARE K.O. DRUM | Gas | 0.5 | 32 | FV/6 | 85 | TEMPERATURE GAUGE | 0-100 | -20-+120 | 100 % overload safety of scale range | IP65 | Silicone Oil | 2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
35 | TG-2271 | - | Required | FUEL GAS K.O. DRUM | Gas | 4.9 | 33.6 | 18.2 | 85 | TEMPERATURE GAUGE | 0-100 | -20-+120 | 100 % overload safety of scale range | IP65 | Silicone Oil | 2" | Manifold Support | 2-VALVE | 300# | PTFE | 1/2" NPTM | S5551 | TW10 | R5503 NS 160 Lower mount (radial) | 160 | dual scale as per data sheet | Stainless steel 316L | Stainless steel 316L | The accuracy is ±1%. | Stainless steel 316SS | Stainless steel 316L | Stainless steel | Laminated safety glass | EN 13190
| commissioning spare part | DESCRIPTION | QTY. |  | 2YEARS SPARE PART | DESCRIPTION | QTY.
|  | Similar to tag TG-2111 | 1 |  |  | Similar to tag TG-2111 | 2
|  | Similar to tagTG-2123A | 1 |  |  | Similar to tagTG-2123A | 2