## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE FOR FLARE PACKAGES
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 17
9184 – 073 - 053 |  |  |  | BK |  | GCS | PEDCO | 120 |  | ME | TB | 0012 | D00
طرح نگهداشت و افزایش تولید 27 مخزن
TBE FOR FLARE PACKAGE نگهداشت و افزایش تولید میدان نفتی بینک
D00 |  |  | JUN.2023 |  | IFI |  |  |  | H.Adineh |  |  | M.Fakharian |  | A.M.Mohseni
Rev. |  |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 | 3 |  |  |  | CLIENT Doc. Number: |  |  |  | F0Z-709238
status: |  | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE FOR FLARE PACKAGES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 17
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | ME | TB | 0012 |  | D00
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | [7 empty] | 65
2 | X | [7 empty] | 66
3 | X | [7 empty] | 67
4 | X | [7 empty] | 68
5 | X | [7 empty] | 69
6 | X | [7 empty] | 70
7 | X | [7 empty] | 71
8 | X | [7 empty] | 72
9 | X | [7 empty] | 73
10 | X | [7 empty] | 74
11 | X | [7 empty] | 75
12 | X | [7 empty] | 76
13 | X | [7 empty] | 77
14 | X | [7 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## PK-2101
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE FOR GAS FLARE PACKAGES
|  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
شماره پیمان: |  | BK | GCS |  | PEDCO |  | 120 | ME | TB |  | 0012 |  | D00
053 – 073 - 9184
REQ. NAME: Material Requisition for Flare packages | [5 empty] | BIDDER: |  |  |  | "A" |  |  | "B" |  | "C" |  | "D"
REF. REQ. NO. : BK-GCS-PEDCO-120-ME-MR-0012 | [5 empty] | NAME: |  |  |  | Takestan
EQUIPMENT TYPE: Flare packages
NO OF ITEMS INCLUDED IN REQUISITION: FST-2201, IG-2201
NO. | DESCRIPTION |  |  | UNITS |  | TECHNICAL REQUIREMENTS |  |  |  | MEETS TECHNICAL REQUIREMENT
[10 empty] | DESCRIPTION |  | STATUS | DESCRIPTION | STATUS | DESCRIPTION | STATUS | DESCRIPTION | STATUS
1. GENERAL
1.1 | Scope of Supply and Work |  |  | NO. | NO. | Material Requisition |  |  |  | CONFIRM
1.2 | Codes and Standards |  |  |  |  | Material Requisition |  |  |  | CONFIRM
1.3 | Reference List |  |  |  |  | to be Supplied by Bidder |  |  |  | CONFIRM
1.4 | Quality Assurance and Relevant Certificates |  |  |  |  | to be Supplied by Bidder |  |  |  | CONFIRM
1.5 | Any Deviation List From MR and Its Attachments. |  |  |  |  | Material Requisition |  |  |  | CONFIRM
1.6 | warrant the engineering, materials and workmanship of the Package. |  |  |  |  | The guarantee period shall be eighteen (18) months from the date of delivery or twelve (12) months from the installation date of each equipment/packages at site. |  |  |  | CONFIRM
1.7 | Design Life |  |  |  |  | 20 Years |  |  |  | CONFIRM
1.8 | Emission Limits at Groung Level |  |  |  |  | to be defined and guaranteed by Bidder |  |  |  | CONFIRM
1.9 | Delivery Time and Time Schedule |  |  |  |  | to be Dfined by Bidder |  |  |  | CONFIRM
1.10 | Delivery Condition and Place |  |  |  |  | to be Dfined by Bidder |  |  |  | CONFIRM
1.11 | Erection , Commissioning and 2 Years Spare |  |  |  |  | AS per Project specification NO. E&C-QC-SP-1 |  |  |  | CONFIRM
1.12 | Performance Guarantee Based on Duty Specification and Mechanical Specification |  |  |  |  | As per Mechanical Data sheet |  |  |  | CONFIRM
2. MECHANIC
2.1 | Stack Support |  |  |  |  | To be Defined By Bidder |  |  |  | GUY WIRE
2.2 | Stack Height (Iinclude Tip Height) |  |  | m |  | 22.5(Vendor to be verified) |  |  |  | 22.5 m
2.3 | Stack Size |  |  | inch |  | To be Defined By Bidder |  |  |  | 12''
2.4 | Flare Stack Material(as minimum) |  |  |  |  | C.S.+3mm(VTA) |  |  |  | C.S. +3mm
2.5 | Flare Tip Length |  |  | m |  | To be Defined By Bidder |  |  |  | 3 M
2.6 | Flare Tip Size |  |  | inch |  | To be Defined By Bidder |  |  |  | 12''
2.7 | Flare Tip Material |  |  |  |  | S.S.310(VTC) |  |  |  | S.S.310
2.8 | Number of Pilot |  |  |  |  | Min. 3 Pilot |  |  |  | CONFIRM
2.9 | Pilot Material |  |  |  |  | S.S.304(VTC) |  |  |  | S.S.304
2.1 | Ignition Type and System |  |  |  |  | High Energy Generator |  |  |  | CONFIRM
2.11 | Flare Burner Internal Lining |  |  |  |  | To be Defined By Bidder |  |  |  | 2''
2.12 | Flare Gas Seal Type |  |  |  |  | Dynamic seal |  |  |  | CONFIRM
2.13 | Flare Gas Seal Material |  |  |  |  | To be Defined By Bidder |  |  |  | stainless steel
2.14 | Distance Between Ignition Panel and Pilot Burners |  |  | m |  | ~100 m |  |  |  | CONFIRM
2.15 | Corrosion allowance |  |  | mm |  | CS pressure part: 3.2 mm No Corrosion allowance for SS |  |  |  | CONFIRM
2.16 | Design Life for flare Tip |  |  | years |  | 25 years |  |  |  | CONFIRM
3. PROCESS
3.1 | F Factor Method |  |  |  |  | To be Defined By Bidder |  |  |  | Generic Pipe
3.2 | Transmissivity Factor |  |  |  |  | To be Defined By Bidder |  |  |  | Calculated Min Value 1.000 Max Value 1.000
3.3 | Heat Release |  |  |  |  | To be Defined By Bidder |  |  |  | 345416.3 Kw
3.4 | Noise Level at Normal and Emergency Condition |  |  |  |  | As Per Ips-G-SF-900 |  |  |  | CONFIRM
3.5 | Solar Radiation |  |  |  |  | As Per BK-GNRAL-PEDCO-000-PR-DB-0001 |  |  |  | CONFIRM
3.6 | Wind Velocity for Radiation Calculations |  |  |  |  | As Per BK-GNRAL-PEDCO-000-PR-DB-0001 |  |  |  | CONFIRM
3.7 | Allowable Pressure Drop |  |  |  |  | To be Defined By Bidder |  |  |  | Tip Pressure Drop 0.015 bar Tip Total Pressure Drop 0.013 bar Seal Pressure Drop 0.000 bar Seal Total Pressure Drop 0.000 bar Stack Pressure Drop 0.056 bar Stack Total Pressure Drop 0.051 bar
3.8 | Mach Number |  |  |  |  | As Per BK-GNRAL-PEDCO-000-PR-DC-0001 |  |  |  | CONFIRM
3.9 | Design Temperature |  |  |  |  | As Per BK-GNRAL-PEDCO-000-PR-DC-0001 |  |  |  | CONFIRM
3.1 | Design Pressure |  |  |  |  | As Per BK-GNRAL-PEDCO-000-PR-DC-0001 |  |  |  | CONFIRM
3.11 | Flow Rate |  |  |  |  | As Per BK-GCS-PEDCO-120-PR-RT-0002 |  |  |  | CONFIRM
3.12 | Smokeless Capacity |  |  |  |  | As Per BK-GCS-PEDCO-120-PR-RT-0002 BK-GCS-PEDCO-120-PR-SP-0003 |  |  |  | CONFIRM
3.13 | Flare GasTemperature |  |  |  |  | As Per BK-GCS-PEDCO-120-PR-RT-0002 BK-GCS-PEDCO-120-PR-SP-0003 |  |  |  | CONFIRM
3.14 | Pilot Gas Flow Rate |  |  |  |  | To be Defined By Bidder |  |  |  | -
3.15 | Pilot Gas Pressure |  |  |  |  | To be Defined By Bidder |  |  |  | 158 Barg
3.16 | Pilot Gas Temperature |  |  |  |  | To be Defined By Bidder |  |  |  | 57 C
3.17 | Utility Consumptions: Fuel Gas LPG Instrument Air Nitrogen Power Steam |  |  |  |  | To be Defined By Bidder |  |  |  | Fuel Gas LPG Instrument Air Nitrogen Power Steam
3.18 | Air flow for Smokeless |  |  |  |  | To be Defined By Bidder |  |  |  | CONFIRM
3.19 | Air pressure for Smokeless |  |  |  |  | To be Defined By Bidder |  |  |  | -
3.20 | Smokeless criteria |  |  |  |  | As Per BK-GCS-PEDCO-120-PR-RT-0002 BK-GCS-PEDCO-120-PR-SP-0003 |  |  |  | CONFIRM
3.21 | Maximum radiant intensities at ground level for cumulated flowrate |  |  | Kw/m² |  | AS PER BK-GCS-PEDCO-120-PR-RT-0024_D04 |  |  |  | CONFIRM
3.22 | Maximum radiant intensities at ground leve |  |  | Kw/m² |  | AS PER BK-GCS-PEDCO-120-PR-RT-0024_D04 |  |  |  | CONFIRM
3.23 | Radius of sterile area from stack based on 4.73 Kw/m² radiation intensity. |  |  | m |  | AS PER BK-GCS-PEDCO-120-PR-RT-0024_D04 |  |  |  | CONFIRM
3.24 | Flare Monitoring |  |  |  |  | Yes |  |  |  | CONFIRM
3.25 | Flare Restricted area affected zone by toxic gas dispersion (m) |  |  | m |  | Not Reached |  |  |  | CONFIRM
3.26 | Gas Back Up (LPG Bottle for Pilot) |  |  | Hr |  | 12 |  |  |  | CONFIRM |  |  | 24 Hr
3.27 | Automatic Re-Ignation System |  |  |  |  | Yes |  |  |  | CONFIRM
3.28 | Internal Combustion Detector |  |  |  |  | Yes |  |  |  | CONFIRM
4. Electrical Requirements
4.1 | Design electrical specification as per JOB SPECIFICATION FOR DESIGN ELECTRICAL INSTALLATION IN PACKAGES. |  |  |  |  | BK-GNRAL-PEDCO-000-EL-DC-0001 |  |  |  | CONFIRM
4.2 | Design and supply of ACWL Local control panel and distribution board shall be in accordance withAnnex 14 of ICAO; JOB SPECIFICATION FOR SUPPLY DISTRIBUTION PANELS. |  |  |  |  | According to Annex 14 of ICAO (Manufacture Standard) |  |  |  | CONFIRM
4.3 | Electrical voltage and phase |  |  |  |  | 400/230 V ±5 %, 50 Hz ±2 %, |  |  |  | CONFIRM
4.4 | Degree of protection |  |  |  |  | Motor: IP 54 Terminal Box of Motor: IP 55 LCS/LCP: IP 54 |  |  |  | CONFIRM
4.5 | Hazardous Area Classification |  |  |  |  | Safe Area |  |  |  | CONFIRM
4.6 | The aircraft warning lights (ACWL) shall be: - LED or long life neon lamps. - Twin unit. - Type B. - 230 VAC/ 50 Hz. - Red color. RAL 6021. - Medium intensity (MIOL), Flashing type for top level. - Low intensity (LIOL), Fixed type for middle level. - 3 sets twin ACWL shall be spaced at 120° around each level of stack - Refer to ICAO standard, Spacing between two level of lights shall be maximum 45 meters. |  |  |  |  | Required |  |  |  | CONFIRM
4.7 | Only 1 feeder (line) 3Ph/400VAC/50Hz will be supplied by purchaser for each flare and all Non-UPS loads (ACWL Blower, Sidt Panel, etc.) shall be distributed by vendor and to be fed from the aforesaid feeder. |  |  |  |  | - |  |  |  | -
4.8 | Air Blower Power Rated & Quantity |  |  | KW/ No |  | to be Dfined by Bidder |  |  |  | CONFIRM
4.9 | Air Blower VFD Quntity |  |  |  |  | if Required |  |  |  | VFD is required
4.10 | Electrical specification of VFD |  |  |  |  | if Required |  |  |  | VFD is required
4.11 | VFD Manufacturer |  |  |  |  | if Required |  |  |  | VFD is required
5. Instrument
5.1 | Remote control for flare ignition |  |  |  |  | required as per Project P&ID |  |  |  | CONFIRM
5.2 | control system type |  |  |  |  | TYPE A as per project Spec. BK-GNRAL-PEDCO-000-IN-SP-0004 |  |  |  | CONFIRM
5.3 | Temprature indicators on ignition panels |  |  |  |  | required as per Project P&ID |  |  |  | CONFIRM
5.4 | K type thermocouples dual type for each pilots |  |  |  |  | required as per Project P&ID |  |  |  | CONFIRM
5.5 | Number of thermocouple |  |  |  |  | 3 Nos. |  |  |  | CONFIRM
5.6 | Area Clasification/IP rating |  |  |  |  | Zone 2 / IP65 |  |  |  | CONFIRM
5.7 | Explosive Proof Grade |  |  |  |  | EEx requirments |  |  |  | CONFIRM
5.8 | Thermocouple cable ( from flare tip to IGP, Estimated length 250) | [8 empty] | CONFIRM
5.9 | Flame detector for pilots |  |  |  |  | required as per Project P&ID |  |  |  | CONFIRM
5.10 | Pilot status indication on ignition panel |  |  |  |  | required as per Project P&ID |  |  |  | CONFIRM
5.11 | on/off push button for pilots on ignition panel | [8 empty] | CONFIRM
5.12 | All instrumentation, tube& fitting , Jb, Cable , earthing,… inside package skid |  |  |  |  | required as per Project documents |  |  |  | CONFIRM
5.13 | Spare part |  |  |  |  | required as per Project PMR |  |  |  | CONFIRM
5.14 | Special tools |  |  |  |  | required as per Project PMR |  |  |  | CONFIRM
5.15 | documentation |  |  |  |  | required as per Project PMR |  |  |  | CONFIRM
5.16 | Test and inspection |  |  |  |  | required as per Project PMR |  |  |  | CONFIRM
6. Piping Requirements
6.1 | Design Code |  |  |  |  | ASME B31.3 |  |  |  | CONFIRM
6.2 | Tie in Points |  |  |  |  | to be Dfined by Bidder |  |  |  | ACC to P&ID
6.3 | Piping Material: |  |  |  |  | AS PER BK-GCS-PEDCO-120-PI-SP-0001_D02 |  |  |  | CONFIRM
6.4 | Painting Equipment |  |  |  |  | AS PER BK-GNRAL-PEDCO-000-PI-SP-0006_D04 |  |  |  | CONFIRM
6.5 | Stress Analysis Calculation |  |  |  |  | CAESAR II |  |  |  | CONFIRM
6.6 | 3D Model of Whole Package in PDMS Format |  |  |  |  | PDMS 12.1 |  |  |  | CONFIRM
6.7 | Pipe and piping specification |  |  |  |  | PIPING MATERIAL SPECIFICATION |  |  |  | CONFIRM
7. Structure
7.1 | Provide foundation load and anchor bolts drawings for Purchaser to design foundation. Also structure calculations . | [8 empty] | CONFIRM
7.2 | structural supports are Galvanized carbon steel type ISO-2408 group3. | [8 empty] | CONFIRM
7.3 | Structural Steel Material | [8 empty] | CONFIRM
7.4 | Structural bolts materials | [8 empty] | CONFIRM
7.5 | for all structural parts ASCE7-10 and AISC loading and design requirements shall be considered more than codes specified in datasheets. | [8 empty] | CONFIRM
7.6 | Bolts, nuts and gratings surface coating | [8 empty] | CONFIRM
7.7 | AISC 13th (2016) - steel construction manual (specially AISC 341 and AISC 360) shall be considered as design codes and standards and ASCE 07-05/10 for structure loading shall be considered as loading codes and standards. | [8 empty] | CONFIRM
7.8 | The latest edition (2014 or 2019) should be followed for ACI318 design code. | [8 empty] | CONFIRM
7.9 | Canopy B115:J123for motors which are exposed to sun light shall be considered | [8 empty] | CONFIRM
8. SAFETY
8.1
8.2
8.3
8.4
8.5
8.6
9. SPARE PARTS
9.1 | Spare parts for pre commissioning and commissioning |  |  | - |  | As per E&C-QC-SP-1 |  |  |  | CONFIRM
9.2 | Spare parts list for two (2) years operation {Option} |  |  | - |  | As per E&C-QC-SP-1 |  |  |  | CONFIRM
9.3 | Capital spare parts {Option} |  |  | - |  | Bidder To Specify |  |  |  | not Required
11. EXCEPTION & DEVIATION
10.1 | Filled in and signed off deviation form |  |  | - |  | Y / N / N.A. |  |  |  | CONFIRM
12. DELIVERY AND SHIPMENT
11.1 | Delivery term |  |  | - |  | Bidder To Specify |  |  |  | 6 months and delivered form the factory
11.2 | Delivery time |  |  | - |  | Bidder To Specify |  |  |  | 6 months
| FINAL CONCLUSION | [8 empty] | ACCEPTED |  |  | ACCEPTED |  | ACCEPTED |  | ACCEPTED
Notes: 1) ABBREVIATIONS: Y: ACCEPTED By Bidder, N: NOT ACCEPTED By Bidder, N.A.: NOT APPLICABLE