## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-TB-0003 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2605 |  |  | Transmital Date: 2/27/2024
Document Title: TBE For Existent MV Switchgear Expansion, RCP & MV Capacitor Bank |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-2605 |  |  | Transmital Date: 2/27/2024
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-TB-0003_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Following items shall be added to TCL and completed by vendor in next revision: |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 |  |  |  | Item 8 below.
1-1 | Certificate or license, test reports and type test shall be submitted based on latest revison of related standard especially for MV switchgear such as IP, short circuit level, temperature rise and etc. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید. |  |  | Item 9 below.
1-2 | Vendor is supposed to prepare preliminary substation arrangement drawing for this project and consider dummy panel (if required). See and use attached file as project arrangement document. It is obvious exact number of dummy panels will be specified by vendor. Meanwhile dummy panel(s) shall be similar to other cubicles. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردید. |  |  | Noted and Closed.
1-3 | Exact part list of the Switchgear including equipment name, brand, model and origin shall be submitted considering this TCL. Vendor is responsible for exact part list of the SWG. If any item to be missed from the part list, Vendor shall consider it without any cost & time impact. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | بند 28 به TCL اضافه گردید. |  |  | Noted and Closed.
1-4 | Native completed deviation from Purchase Order or Purchaser procurement documents shall be submitted in next revision. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردید. |  |  | Noted and Closed.
1-5 | All required signals and mapping shall be submitted and considered From/To DCS base on "Electrical I/O Signal List BK-GCS-PEDCO-120-EL-LI-0005". Manufacturer shall consider suitable relays / auxiliary contacts for this reason. Vendor shall confirm necessary facility will be considered. Please follow Electrical I/O Signal List (See attach file). |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | بند 29 به TCL اضافه گردید. |  |  | Noted and Closed.
1-6 | Certificate for country of origin shall be submitted by Vendor (after PO.). Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | بند 26 از TCL اصلاح گردید.
1-7 | Burden of CT’ & PT’s will be finalized after purchase order based on the related calculation that will be submitted by Vendor and shall be approved by Purchaser. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردیید. |  |  | Noted and Closed.
1-8 | The software of the protection relay shall be provided with original licence. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردیید. |  |  | Noted and Closed.
1-9 | All protection relays are equipped with key pan and LCD display, and 7 Numbers Digital input /7 Numbers Dry Output Contacts as minimum which is should be re-checked with schematic diagram. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | بند 32 از TCL اضافه گردید. |  |  | Noted and Closed.
1-10 | All relays supplied with MV switchgear shall be microprocessor based, which will facilitate a connection to DCS. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید. |  |  | Noted and Closed.
1-11 | Vendor shall perform programming of the relays based on requirements of logic diagram. Related documents shall be submitted. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید. |  |  | Noted and Closed.
1-12 | Vendor shall perform relay setting and relay coordination based on project relay coordination and setting study. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید. |  |  | Noted and Closed.
1-13 | All digital multimeters and protection relays shall have Mod Bus (RS 485) communication protocol. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید. |  |  | Noted and Closed.
2 | Following description shall be added to Item 1 in TCL: Vendor shall submitted temperature de‐rating factors of equipment such as CB, etc. It means Vendor shall de-rate the rated current of equipment on the site condition such way that de-rated rated current be equal or higher than rate current. De-rating curves/Tables (altitude & Ambient Temperature) shall be submitted at this stage. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید. |  |  | Noted and Closed.
3 | Following description shall be added to Item 7 in TCL: Sub vendor list shall be submitted and following items shall be specified in sub vendor list: -Manufacture -Country of origin -Model Consideration shall be given that |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردید. |  |  | Noted and Closed.
4 | Item 8 in TCL shall be modified as below: Based on the 22-E&C-QC-SP-1,Spare parts for pre-commissioning, commissioning/start up and spare parts for two years shall be submitted separately based on Spare Parts Specification. The supplied spare parts shall comply with the same specifications as the original parts and shall be interchangeable with the original parts without any modification. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید. |  |  | Noted and Closed.
5 | Item 18 in TCL shall be modified as below: All the following items shall be considered in proposal for all Vacuum Circuit Breakers: Anti-pumping device, Mechanical operations counter, Manual mechanical trip facility Closed/open position indication, Start/Stop & Emergency Stop push button, Charged/discharged spring indication, Emergency shutdown interposing relay and Minimum 4 numbers make contacts. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردید. |  |  | Noted and Closed.
6 | All manufacturers shall be considered based on MOP. Any deviation from MOP is not acceptable. For example it shall be checked for Petro Tajhiz Iliya. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | شرکت ایلیاتجهیز حذف گردید. |  |  | Noted and Closed.
7 | Complimentary comments will be submitted after submitting revised technical offer based on comments. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | در صورت وجود کامنت های دیگر، این کامنتها در نظر گرفته خواهد شد. |  |  | Noted and Closed.
8 | Item 1 above: TCL shall be filled by vendor and submitted in next technical offer. Moreover, all mentioned documents in TCL shall be submitted by vendor. Otherwise, it will not be acceptable. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
9 | Item 1-1 above: Not accepted. It has not been implemented correctly in TCL by consultant. Related certificate, license, type test and test reports are necessary to submit by vendor at the bid stage to check the quality and capability of vendor. It is very strange that the vendors has not submitted above mentioned documents while has been accepted in TBA by consultant. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
10 | All attached document to MR shall be signed, stamped and submitted by vendor at this stage such as Existent MV Switchgear Expansion Single Line Diagram, Electrical I/O Signal List, Electrical Equipment Arrangement Layout for Building, etc. for example Pars Tableau has not submitted above mentioned documents. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
11 | Technical offer shall be submitted completely for example 3.3KV switchgear, MV capacitor bank and RCP has not been submitted by Pars Tableau. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
12 | All data sheet shall be filled completely by vendor correctly and submitted. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
13 | All deviations shall be filled in native deviation list by vendor (According to TCL) and shall be clarified between consultant and vendor. Then, the results shall be reflected into TBA conclusion. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
14 | All catalogues of electrical equipment such as ACB, protection relay, capacitor bank, etc. shall be submitted by vendor. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
15 | Capacitor bank single line diagram shall be signed and stamped by vendors. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
16 | Guarantee period shall be added to TBE table. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
17 | Due to new MV switchgear cells to be installed in the existing switchgear building and there are limitation in free space, all Bidders to be issued their preliminary arrangement layout including proposed cells dimensions in order to checking installation ability in the available free space. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
18 | Pars Tablo: |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
18-1 | As per MR "which ever comes earlier" phrase shall be deleted from guarantee period in the Pars Tablo technical offer page 5. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
18-2 | Cell width in the Pars Tablo offer is 900mm but existing cells width is 750mm and equipment arrangement document (BK-GCS-PEDCO-120-EL-PY-0008_D03 ) prepared based on 750mm width for new cells. This item need to check by Consultant due to lack of required space in the switchgear building |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
18-3 | Cell depth in the Pars Tablo offer is 2225mm while existing cells depth is 2000mm. and equipment arrangement document (BK-GCS-PEDCO-120-EL-PY-0008_D03 ) prepared based on 2000mm depth for new cells. This item need to check by Consultant due to lack of required space in the switchgear building |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
18-4 | Capacitor bank, RCP and 3.3kV cell not exist in the Pars Tablo technical offer, how Hirgan did the TBE without technical offer? |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
18-5 | lockout relay 86T has not been considered in the Pars Tablo offer for JT01, 02,03,04. this item to be clarified with the Bidder. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
18-6 | Capacitor bank single line diagram missed from MR attachments. This document shall be send to the Bidders. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
19 | Runin Sanat: |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
19-1 | Proposed lockout relay 94 instead of 86T will be acceptable in case of relay 94 has manual reset capability. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
19-2 | Runin Sanat proposed two cells for 3.3kV switchgear, but in the switchgear equipment arrangement layout, only one cell has been considered. it shall be checked for possibility for layout arrangement. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
19-3 | proposed cells dimensions (HeightxWidthxDepth) shall be specified in the technical proposal. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
19-4 | Proposed IP41 can be acceptable only in case of NISOC approval. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
20 | Taban Tablo: |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
20-1 | Proposed IP41 can be acceptable only in case of NISOC approval. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
20-2 | Taban Tablo proposed two cells for 3.3kV switchgear, but in the switchgear equipment arrangement layout, only one cell has been considered. it shall be checked for possibility for layout arrangement. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
20-3 | As per latest capacitor bank single line diagram (TR-2325) MV circuit breaker or load break switch is not required for capacitor bank. Proposal shall be modified. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
20-4 | Regarding latest revision of RCP wiring diagram (Tr-2056) required Start/Stop pushout is 10Nos but in the Taban Tablo technical proposal it has been considered 6 Nos. for each. This item to be clarified and modified based on latest revision of engineering documents. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
20-5 | proposed cells dimensions (HeightxWidthxDepth) shall be specified in the technical proposal. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: