## Cover (hidden)
Azar Oil Field Development Central Processing Facilities "EP"-TBE for Fire Water Pumps
Document No.: |  | ARCP-E270GG-ENMA-REEV-0003 | Contract No.: AP-1-92-92 |  |  | Page 1Of 7
"EP"-TBE for Fire Water Pumps
D00 | Issued for Comment |  | M.Kazemi | A.F.Hashemi | M.N.Malayeri
Rev. | Description |  | Prepared By | Checked By | Approved By | Date

## Tabulation (hidden)
Azar Oil Field Development Central Processing Facilities "EP"-TBE for Fire Water Pumps
Document No.: |  | ARCP-E270GG-ENMA-REEV-0003 |  |  |  |  | Contract No.: AP-1-92-92 |  |  |  |  | Page 2 Of 7
Tabulation Of Revised Pages
| Page | Q00 | D01 | D02 | D03 | D04 | Page | D00 | D01 | D02 | D03 | D04
| 1 | x |  |  |  |  | 36
| 2 | x |  |  |  |  | 37
| 3 | x |  |  |  |  | 38
| 4 | x |  |  |  |  | 39
| 5 | x |  |  |  |  | 40
| 6 | x |  |  |  |  | 41
| 7 | x |  |  |  |  | 42
| 8 | [5 empty] | 43
| 9 | [5 empty] | 44
| 10 | [5 empty] | 45
| 11 | [5 empty] | 46
| 12 | [5 empty] | 47
| 13 | [5 empty] | 48
| 14 | [5 empty] | 49
| 15 | [5 empty] | 50
| 16 | [5 empty] | 51
| 17 | [5 empty] | 52
| 18 | [5 empty] | 53
| 19 | [5 empty] | 54
| 20 | [5 empty] | 55
| 21 | [5 empty] | 56
| 22 | [5 empty] | 57
| 23 | [5 empty] | 58
| 24 | [5 empty] | 59
| 25 | [5 empty] | 60
| 26 | [5 empty] | 61
| 27 | [5 empty] | 62
| 28 | [5 empty] | 63
| 29 | [5 empty] | 64
| 30 | [5 empty] | 65
| 31 | [5 empty] | 66
| 32 | [5 empty] | 67
| 33 | [5 empty] | 68
| 34 | [5 empty] | 69
| 35 | [5 empty] | 70

## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE FOR INSTRUMENT/PLANT AIR & NITROGEN PACKAGES
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 7
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | ME | TB | 0006 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
TBE FOR INSTRUMENT/PLANT AIR & NITROGEN PACKAGES نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | JUL.2024 |  | IFI |  |  |  | V.Amjadi |  |  | M.Fakharian |  | M.Sadeghian
D02 |  | FEB.2024 |  | IFI |  |  |  | H.Ghadyani |  |  | M.Fakharian |  | S.Faramarzpour
D01 |  | OCT.2023 |  | IFI |  |  |  | H.Ghadyani |  |  | M.Fakharian |  | S.Faramarzpour
D00 |  | MAR.2023 |  | IFI |  |  |  | H. Adineh |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 3 |  |  |  | CLIENT Doc. Number: F0Z-709228
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE FOR INSTRUMENT/PLANT AIR & NITROGEN PACKAGES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 7
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | ME | TB | 0006 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | X | [5 empty] | 67
4 | X | X | X | [5 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X |  | X |  |  |  | 70
7 | X | X | X | [5 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Instrument,Plant Air
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE FOR INSTRUMENT/PLANT AIR & NITROGEN PACKAGES
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 7
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | ME | TB | 0006 | D03
REQ. NO: BK-GCS-PEDCO-120-ME-MR-0006 |  |  |  | BIDDER NAME: |  | HAVAYAR |  |  | HAVASAN |  | PARS COMPRESSOR |  | ARAZ SANAT ASIA
QUOTATION NO.: | [5 empty] | HY/02/I/3106 |  |  | HAV-BK-HRGN-001 |  | 18910 |  | ASA-LR-02-263
QUOTATION DATE: | [5 empty] | 24/1/2024 |  |  | 2023-08-30 |  | 2023-09-01 |  | 22/1/2024
No. | DESCRIPTION |  |  | UNITS | REQ'D BY PURCHASER | MEETS REQUISITION REQUIREMENTS
[6 empty] | Bidder's Proposal |  | Status | Bidder's Proposal | Status | Bidder's Proposal | Status | Bidder's Proposal | Status
Instrument & Plant Air Production Package
1 | GENERAL
1.1 | Guarantee & Warranty as per project requirement |  |  | - | 12 month after succesfull start up or 18 month after delivery at site | A |  | YES | A | YES | A | YES | A | YES
1.2 | Delivery Time |  |  | Month | As per project requirement | 9 |  | YES | 8 | YES | 12 months Bacuse of UCP (PLC S7 400 FH delivery time) | YES | As per project requirement | YES
1.3 | Delivery Location |  |  | - | - | Ex - work Havayar Factory |  | YES | TABRIZ-HAVASAN | YES | DDP @ site | YES | As per project requirement | YES
2 | DOCUMENTS CHECK LIST
2.1 | Quality System Certificates |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.2 | Catalogues |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.3 | Sub-Vendor List |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.4 | Scope of Supply & Work (Attachment of MR) |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.5 | Deviation List |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.6 | Reference and Installation List |  |  | - | Required | A |  | YES | A | NO | A | YES | A | YES
2.7 | Recommended Spare Part List for erection & Commissioning |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.8 | Recommended Spare Part List for 2 Years of Operation |  |  | - | Required | A |  | YES | NS | NO | A | YES | A | YES
2.9 | Special Tools List (If Required) |  |  | - | Required | NA |  | NO | NA | NO | NA | NO | A | YES
2.1 | P&ID |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.11 | Process Flow diagram |  |  | - | Required | A |  | YES | NS | NO | A | YES | A | YES
2.12 | Control Philosophy |  |  | - | Required | After PO |  | YES | N | NO | After P.O. | YES | A | YES
2.13 | ESD Philosophy |  |  | - | Required | NA |  | NO | N | NO | After P.O. | YES | A | YES
2.14 | Main Equipment list |  |  | - | Required | A |  | YES | After P.O. | YES | A | YES | A | YES
2.15 | Calculation Note For PSV Sizing |  |  | - | Required | A (PSV Sizing on skid is as per manufacturer design and standard) |  | YES | NA | NO | After P.O. | YES | A | YES
2.16 | Operating Manual |  |  | - | Required | After PO |  | YES | After P.O. | YES | After P.O. | YES | A | YES
2.17 | Outline/General Lay-out Drawings |  |  | - | Required | A |  | YES | After P.O. | YES | After P.O. | YES | A | YES
2.18 | Data Sheets for All Equipment Inside the Package |  |  | - | Required | A |  | YES | After P.O. | YES | After P.O. | YES | A | YES
2.19 | Performance Curve |  |  | - | Required | A |  | YES | After P.O. | YES | After P.O. | YES | A | YES
2.2 | Utility Consumption List |  |  | - | Required | A |  | YES | NS | NO | A | YES | A | YES
2.21 | Load List |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.22 | Control System Architecture Drawing |  |  | - | Required | A |  | YES | After P.O. | YES | A | YES | A | YES
3 | SCOPE OF SUPPLY
3.1 | Oil Free Screw Compressors |  |  | - | 2 (1+1) | A |  | YES | A | YES | A | YES | A | YES
3.2 | Coupling with Non-sparking Guard |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
3.3 | Pressurized Lubrication System |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
3.4 | Drivers (Electro motor) and Accessories, Space Heater |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
3.5 | Gearbox |  |  | - | Required | A |  | YES | A | YES | A | YES | NA | YES
3.6 | Inlet Air Filter and Silencer |  |  | - | Required | A (Blow down discharge silencer has been considerd) |  | YES | A | YES | A | YES | A | YES
3.7 | Accessories for Inlet Filter Cleaning |  |  | - | Required | NA |  | NO | NA | NO | PDT | YES | A | YES
3.8 | Interstage air cooler and water separator and water trap |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
3.9 | After cooler, Outlet water separator(at down stream of after (with water trap cooler |  |  | - | Required | A |  | YES | N (WATER TRAP) | NO | A | YES | A | YES
3.10 | Capacity Control system |  |  | - | Required | Blow down valve has been considered . Compressor is load/unload |  | YES | A | YES | A | YES | A | YES
3.11 | Air Dryer Package |  |  | - | 2 (1+1 column) | A |  | YES | A | YES | A | YES | A | YES
3.12 | Instrumentations (Minimum as per PID & duty spec) |  |  | - | Required | N (AS Per HAVAYAR P&ID) |  | NO | NA | NO | A | YES | A | YES
3.13 | Unit Control panel and local board dedicated to each Air Compressor and Dryer As per Project requirements (Air Package) |  |  | - | Required | 2 Unit Control panel |  | YES | N | NO | A | YES | A | YES
3.14 | Acoustic Enclosure (if any) |  |  | - | Required | A |  | YES | NA | YES | A | YES | NA | YES
3.15 | Mating Flanges with Bolts, Nuts and Gasket (If Required) |  |  | - | Required | NA |  | YES | A | YES | A | YES | A (ON SKID) | YES
3.16 | Grounding Bosses & Wiring |  |  | - | Required | A (ON SKID) |  | YES | N (for air receiver) | NO | A (Earthin lugs + wiring inside the package BL) | YES | A (ON SKID) | YES
3.17 | Ladders, Stairs, Platforms and Hand Railings,etc., Within the Package |  |  | - | Required | NA |  | YES | N(for air receiver) | NO | A | YES | A (ON SKID) | YES
3.18 | All Interconnecting Piping, Valves and Fittings |  |  | - | Required | A (ON SKID) |  | YES | NS | NO | A | YES | A (ON SKID) | YES
3.19 | All Electrical and Instrumentation Cabling |  |  | - | Required | A (ON SKID) |  | YES | NS | NO | A | YES | A (ON SKID) | YES
3.2 | All Electrical and Instrumentation Junction Boxes |  |  | - | Required | A (ON SKID) |  | YES | NS | NO | A | YES | A (ON SKID) | YES
3.21 | All Required Cable Trays, Tray Support and Cable Transits |  |  | - | Required | A (ON SKID) |  | YES | NS | NO | A | YES | A (ON SKID) | YES
3.22 | Foundation Bolts and Nuts |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
3.23 | Name Plates for All Equipment |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
3.24 | Lifting Frames or Beams Including Slings and Shackles |  |  | - | Required | A ( LIFTING LUG HAS BEEN CONSIDER) |  | YES | N (for air receiver lifting lug) | YES | NA | YES | A | YES
3.25 | All Insulation and Heat Tracing |  |  | - | Required | NA |  | YES | NA | YES | NA | YES | A | YES
2.26 | First Filling |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
3.27 | Personnel Safety Devices |  |  | - | Required | NA |  | YES | NA | YES | A | YES | A | YES
4 | SCOPE OF WORK
4.1 | Engineering & Documentation |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.2 | Manufacturing & Assembling |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.3 | PIM (pre-inspection meeting) |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.4 | Procurement |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.5 | Inspection & Testing at shop |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.6 | Performance Guarantee |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.7 | Mechanical Guarantee |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.8 | Review of Purchaser’s Drawings |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.9 | Painting |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.1 | Shipping and Transportation |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.11 | Packing & Preservation |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.12 | Certification |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.13 | Coordination with Sub vendors |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.14 | Export Customs Clearance |  |  | - | Required | NA |  | YES | N | NO | A | YES | A | YES
4.15 | Obtain Any Export License or Other Official Authorization |  |  | - | Required | A |  | YES | N | NO | NA | YES | A | YES
4.16 | Supervision for Installation |  |  | - | Required (As Option) | A |  | YES | A | NO | A | YES | A | YES
4.17 | Supervision for Pre-commissioning, commissioning & Start up |  |  | - | Required (As Option) | A |  | YES | A | NO | A | YES | A | YES
4.18 | Vendor Shop Training for Owner’s Personnel |  |  | - | Required (As Option) | A |  | YES | A | NO | A | YES | A | YES
4.19 | Insulation Work (If any) |  |  | - | Required | NA |  | YES | NA | YES | NA | YES | A | YES
5 | SITE CONDITION
5.1 | Ambient temperature (Max./Min.) |  |  | °C | 5~50 | A |  | YES | A | YES | A | YES | A | YES
5.2 | Relative Humidity (Max./Min.) |  |  | % | 0~100% | A |  | YES | A | YES | A | YES | A | YES
5.3 | Barometric Pressure |  |  | bara | 0.914~0.991 | A |  | YES | A | YES | A | YES | A | YES
6 | OIL FREE SCREW COMPRESSORS
6.1 | Quantity |  |  |  | 2 (1+1) | A |  | YES | A | YES | A | YES | A | YES
6.2 | Manufacturer |  |  | - | VTS | HAVAYAR |  | YES | HAVASAN- AirEnd GHHRAND | YES | GHH Rand | YES | GHH | YES
6.3 | Compressor Allowable Operating Temperature (Max. / Min.) |  |  | - | 5/50 | A |  | YES | A | YES | A | YES | A | YES
6.4 | Delivered Flow |  |  | Nm³/hr | VTS | 170.8 |  | A | 438 @ Site | YES | 235 | YES | 191 | YES
6.7 | Design Capacity (Dry Basis) |  |  | Nm³/hr | 191 | A |  | YES | 487 @ 20 °C , 0%, 1 atm | YES | 235 | YES | A | YES
6.5 | Design Pressure |  |  | barg | 12.5 | A |  | YES | A | YES | A | YES | A | YES
6.6 | Package Outlet Air Pressure |  |  | barg | 9.5 | A |  | YES | A | YES | A | YES | A | YES
6.9 | Dry Air Pressure at Normal Conditions at Producer's B/L |  |  | barg | 9 | A |  | YES | A | YES | A | YES | A | YES
6.10 | Max. Outlet Air temperature @ after cooler outlet |  |  | °C | 65 | 60 |  | NO | A | YES | A | YES | A | YES
6.11 | Max Dust Particle Size |  |  | - | ≤ 0.1 µm | A |  | YES | A | YES | A | YES | A | YES
6.12 | Noise Level |  |  | dB(A) | < 85 | A |  | YES | A | YES | A | YES | A | YES
6.13 | Capacity Control Method |  |  | - | Load/Unload | A |  | YES | A | YES | A | YES | A | YES
6.14 | Cooling Type |  |  | - | Air Cooled | A |  | YES | A | YES | A | YES | A | YES
6.15 | Intake Filter |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
6.16 | Air-end Manufacturer / Model |  |  | - | VTS | GHH Rand/CD8D |  | YES | AirEnd GHHRAND - CD 8D | YES | GHH Rand/CD8D | YES | GHH | YES
6.17 | Power Transmission Method |  |  | - | Direct Coupled or Gear Type | Gear Type |  | YES | Gear Type | YES | Direct Coupled | YES | Direct Coupled | YES
6.18 | Weight |  |  | kg | VTS | 1817 |  | YES | 1900 | YES | NS | NO | according catalogue of compressor & dryer | YES
6.19 | Dimension (L x W x H) |  |  | mm | VTS | 2240 x 1370 x 1985 |  | YES | 2000 x 1200 x 1650 | YES | 2450x1300x1950 | YES | according catalogue of compressor & dryer | YES
6.20 | Enclosure Fan Motor Power / Qty |  |  | kW | VTS | 5.5 |  | YES | 4 | YES | N | NO | 5.5/A | YES
6.21 | Room Mounted Control Panel per compressor |  |  | - | PLC Type C | A |  | YES | NS (refer to last Deviation list) | NO | A | YES | PLC Type C | YES
6.22 | SIL Rated loops for safety functions |  |  |  | Required | N |  | YES | NS | NO | N ( SIL studey by EPC contractor) | YES | A | YES
6.23 | Control Panel Power ( UPS/Non UPS) |  |  | KW | 110VAC/230VAC | 2KW/1.5KW (For each UCP as Per HAVAYAR Load list |  | YES | NS | NO | A | YES | A | YES
6.24 | Instrumentation/Analyzer |  |  |  | As per Specification | Noted by considering deviation list/ Dew point transmitter on dryer common header |  | YES | refer to last Deviation list | NO | A (DEWPOINT) | YES | A | YES
6.25 | Local Control Panel |  |  |  | Required per compresssor | Noted only for stop, start and status without control function. Control is by UCP |  | YES | A | YES | A | YES | A | YES
6.26 | Cabling to LCP |  |  |  | Required | A |  | YES | NS | NO | A | YES | A | YES
6.27 | Serial Link connection |  |  | - | Modbus RTU | A |  | YES | NS | NO | A | YES | A | YES
7 | MAIN MOTOR
7.1 | Manufacturer |  |  | - | VTS | JEMCO |  | YES | WEG | YES | JEMCO/OME | YES | ABB/SIEMENS/WEG | YES
7.2 | Motor Power |  |  | - | KW | 55 |  | YES | 55 | YES | 75 | YES | 55 | YES
7.3 | Power Supply |  |  | V / HZ / PH | 400/50/3 | A |  | YES | A | YES | A | YES | A | YES
7.4 | IP Degree / Temperature Class |  |  | - | VTS | 55/B |  | YES | IP 55 Insulation Class=F- Motor Temp. Rise Class: B | YES | 54/T3 | YES | 55/T4 | YES
7.5 | Speed, Motor / Compressor |  |  | rpm | VTS | 3000 |  | YES | 3000 | YES | 2950 | YES | 3000 | YES
8 | AIR DRYER
8.1 | Manufacturer |  |  | - | VTS | HAVAYAR |  | YES | Desiccant Dryer- HAVASN | YES | Par compressor | YES | ASA CO. | YES
8.2 | Type / Design Code |  |  | - | Heatless Desiccant/ASME SEC. VIII DIV.1 & 2 | Heatless Desiccant/ ASME SEC. VIII DIV.1 |  | YES | A | YES | A | YES | A | YES
8.3 | Dryer Life Time |  |  | - | not less than 3 years | A |  | YES | A | YES | A | YES | A | YES
8.4 | Quantity |  |  | - | 2 | A |  | YES | A | YES | A | YES | 2 | YES
8.5 | Desiccant Material |  |  | - | Molecular seive /Activated Alumina | A |  | YES | Molecular seive | YES | A | YES | Carbon Molecular seive | YES
8.6 | Cycle time |  |  | min | VTS | 7~15 |  | YES | 5 | YES | 20 | YES | 5/3/2 | YES
8.7 | Dryer Capacity |  |  | Nm³/hr | VTS | 300 |  | YES | 1080 @ 35 °C , 100%, 7 bar | YES | NS | NO | 175 | YES
8.8 | Inlet Flow Rate |  |  | Nm³/hr | VTS | 140.8 |  | YES | 1080 | YES | 235 | YES | 150 | YES
8.9 | Outlet Flow Rate |  |  | Nm³/hr | 119.7 | A |  | YES | 900 (With max. 20 % purge) | YES | 188 | YES | A | YES
8.10 | Regeneration Flow Ratio |  |  | % | VTS | 15 |  | YES | 20 | YES | 15-20 | YES | 15 | YES
8.11 | Dew Point |  |  | °C | -40 @ 8 barg | A |  | YES | A | YES | A | YES | A | YES
8.12 | Oprating Pressure |  |  | barg | 9 | A |  | YES | A | YES | A | YES | A | YES
8.13 | Design Pressure |  |  | barg | 12.5 | A |  | YES | A | YES | A | YES | A | YES
8.14 | Hydrotest Pressure |  |  | barg | VTS (1.5*MAWP) | 1.3 * Design pressure |  | YES | A | YES | A | YES | A | YES
8.15 | Inlet Temperature |  |  | °C | 60 | A |  | YES | A | YES | A | YES | A | YES
8.16 | Tower Design Code |  |  | - | ASME SEC. VIII DIV.1 | A |  | YES | A | YES | A | YES | A | YES
8.17 | Material for Shell / Head |  |  | - | VTS | SA106 Gr B/SA 234 WPB |  | YES | SA 516 Gr.70 | YES | CS | YES | A516 Gr. 70 | YES
8.18 | Corrosion Allowance |  |  | mm | 3.2 | A |  | YES | A | YES | A | YES | 3.2 | YES
8.19 | Safety Valve |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
8.2 | Pre Filter / Qty. |  |  | - | Required / 2 | A |  | YES | A | YES | A | YES | A/2 | YES
8.21 | After Filter/ Qty. |  |  | - | Required / 2 | A |  | YES | A | YES | A | YES | A/2 | YES
8.22 | Filter Manufacturer |  |  | - | VTS | OMEGA |  | NO | OMEGA AIR | NO | MIKROPOR | NO | Dominic hunter | NO
8.23 | Dryer LCP |  |  | - | Yes , IP65 | A Yes , IP65(LCP include only Stop Start and status without control function) |  | YES | A | YES | IP 55 | NO | A | YES
8.24 | Dryer instrumentation/IP/EEX |  |  | - | As per Specification | IP65, Safe (Non-Ex) |  | YES | NS | NO | A | YES | According PID/54/Safe location | YES
8.25 | Cabling to LCP |  |  |  | Required as per specification | A |  | YES | NS | NO | A | YES | A | YES
8.26 | Dryer Controller Type |  |  | - | Microprocessor | BY UCP |  |  | T1 Designed by CMC | NO | A | YES | PLC | YES
FINAL CONCLUSION | [5 empty] | ACCEPTED |  |  | CONDITIONALLY ACCEPTED(if approved by the CLIENT) |  | ACCEPTED |  | ACCEPTED
NOTES:
ABBREVIATIONS: A: ACCEPTED By Vendor N: NOT ACCEPTED By Vendor NA:Not Applicable NS:Not Specified C:Clarification Required VTS: Vendor to Specify

## N2 Package
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE FOR INSTRUMENT/PLANT AIR & NITROGEN PACKAGES
شماره پیمان: |  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 7
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | ME | TB | 0006 | D03
REQ. NO: BK-GCS-PEDCO-120-ME-MR-0006 |  |  |  |  | BIDDER NAME: |  | HAVAYAR |  |  | HAVASAN |  | PARS COMPRESSOR |  | ARAZ SANAT ASIA
QUOTATION NO.: | [6 empty] | HY/02/I/3106 |  |  | HAV-BK-HRGN-001 |  | 18910 |  | ASA-LR-02-263
QUOTATION DATE: | [6 empty] | 24/1/2024 |  |  | 2023-08-30 |  | 2023-09-01 |  | 22/1/2024
No. | DESCRIPTION |  |  |  | UNITS | REQ'D BY PURCHASER | MEETS REQUISITION REQUIREMENTS
[7 empty] | Bidder's Proposal |  | Status | Bidder's Proposal | Status | Bidder's Proposal | Status | Bidder's Proposal | Status
Nitrogen Production Package
1 | GENERAL
1.1 | Guarantee & Warranty as per project requirement |  |  |  | - | 12 month after succesfull start up or 18 month after delivery at site | A |  | YES | A | YES | A | YES | A | YES
1.2 | Delivery Time |  |  |  | - | As per project requirement | 9 |  | YES | 8 | YES | 14 M (because of UCP S7400 FH delivery time) | YES | As per project requirement | YES
1.3 | Delivery Location |  |  |  | - | As per project requirement | Ex - work Havayar Factory |  | YES | TABRIZ-HAVASAN | YES | DDP At site | YES | As per project requirement | YES
2 | DOCUMENTS CHECK LIST | [12 empty] | `
2.1 | Quality System Certificates |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.2 | Catalogues |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.3 | Sub-Vendor List |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.4 | Scope of Supply & Work (Attachment of MR) |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.5 | Deviation List |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.6 | Reference and Installation List |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.7 | Recommended Spare Part List for erection & Commissioning |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.8 | Recommended Spare Part List for 2 Years of Operation |  |  |  | - | Required | A |  | YES | NS | NO | A | YES | A | YES
2.9 | Special Tools List (If Required) |  |  |  | - | Required | NA |  | NO | NA | NO | NA | NO | A | YES
2.10 | P&ID |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.11 | Process Flow diagram |  |  |  | - | Required | A |  | YES | NS | NO | A | YES | A | YES
2.12 | Control Philosophy |  |  |  | - | Required | After PO |  | YES | N | NO | After P.O. | YES | A | YES
2.13 | ESD Philosophy |  |  |  | - | Required | NA |  | YES | N | NO | After P.O. | YES | A | YES
2.14 | Main Equipment list |  |  |  | - | Required | A |  | YES | After P.O. | YES | A | YES | A | YES
2.15 | Calculation Note For PSV Sizing |  |  |  | - | Required | A PSV Sizing on skid is as per manufacturer design and standard |  | YES | NA | NO | After P.O. | YES | A | YES
2.16 | Operating Manual |  |  |  | - | Required | After PO |  | YES | After P.O. | YES | After P.O. | YES | A | YES
2.17 | Outline/General Lay-out Drawings |  |  |  | - | Required | A |  | YES | After P.O. | YES | A | YES | A | YES
2.18 | Data Sheets for All Equipment Inside the Package |  |  |  | - | Required | A |  | YES | After P.O. | YES | A | YES | A | YES
2.19 | Utility Consumption List |  |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
2.20 | Load List |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
2.21 | Control System Architecture Drawing |  |  |  | - | Required | A |  | YES | After P.O. | YES | A | YES | A | YES
3 | SCOPE OF SUPPLY
3.1 | Pre filter / After Filter / Dust Filter |  |  |  | - | 2/2/1 | 2/2/2 |  | YES | N | NO | A | YES | 2/2/1 | YES
3.2 | Carbon Mole Sieve Adsorption Vessels |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
3.3 | Gearbox |  |  |  | - | Required | A |  | YES | A | YES | A | YES | NA | YES
3.4 | Chiller Package |  |  |  | - | Required | A |  | YES | A | YES | A | YES | NA | YES
3.5 | On-skid piping, tubing & wiring |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
3.6 | Base plate |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
3.7 | Earthing system |  |  |  | - | Required | A (ON SKID) |  | YES | A | YES | A | YES | A | YES
3.8 | Name plates for all equipment |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
3.9 | Any other required accessories |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
3.10 | Commissioning spare parts |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
3.11 | Two years spare parts |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
3.12 | Special tools (if any) |  |  |  | - | Required | NA |  | YES | NA | YES | NA | YES | A | YES
3.13 | First Filling |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
3.14 | Unit Control Panel dedicated to each Nitrogen Package as per project requirements (N2 Package) |  |  |  | - | Required | One Unit Control Panel has been considered for N2 package. Chiller has local controller. |  | YES | A | YES | A | YES | A | YES
3.15 | Personnel Safety Devices |  |  |  | - | Required | NA |  | YES | NA | YES | A | YES | A | YES
4 | SCOPE OF WORK
4.1 | Engineering & Documentation |  |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.2 | Manufacturing & Assembling |  |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.3 | PIM (pre-inspection meeting) |  |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.4 | Procurement |  |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.5 | Inspection & Testing at shop |  |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.6 | PMI for Non-Carbon Steel material |  |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.7 | PWHT/ Stress Relieve (if required) |  |  |  | - | Required | NA |  | YES | N | NO | A | YES | A | YES
4.8 | Chemical Cleaning, Pickling & Passivation for Stainless Steel Parts |  |  |  | - | Required | NA |  | YES | N | NO | A | YES | A | YES
4.9 | Wiring and Tubing to Junction Boxes |  |  |  | - | Required | A (ON SKID) |  | YES | N | NO | A | YES | A | YES
4.10 | Interconnecting piping inside unit assembly |  |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.11 | Review of Purchaser’s Drawings |  |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.12 | Painting |  |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.13 | Participation in HAZOP and SIL Study |  |  |  |  | Required | A |  | YES | N | NO | A | YES | A | YES
4.14 | Shipping and Transportation |  |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.15 | Packing & Preservation |  |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.16 | Certification |  |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.17 | Coordination with Subvendors |  |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.18 | Export Customs Clearance |  |  |  | - | Required | A |  | YES | N | NO | A | YES | A | YES
4.19 | Obtain Any Export License or Other Official Authorization |  |  |  | - | Required | A |  | YES | N | NO | NA | NO | A | YES
4.2 | Supervision for Installation |  |  |  | - | Required (As Option) | A |  | YES | A | YES | A | YES | As Option | YES
4.21 | Supervision for Pre-commissioning, commissioning & Start up |  |  |  | - | Required (As Option) | A |  | YES | A | YES | A | YES | As Option | YES
4.22 | Vendor Shop Training for Owner’s Personnel |  |  |  | - | Required (As Option) | A |  | YES | A | YES | A | YES | As Option | YES
4.23 | Insulation Work (If any) |  |  |  | - | Required | NA |  | YES | NA | YES | A | YES | A | YES
5 | SITE CONDITION
5.1 | Ambient temperature (Max./Min.) |  |  |  | °C | 5~50 | A |  | YES | A | YES | A | YES | A | YES
5.2 | Relative Humidity (Max./Min.) |  |  |  | % | 0~100% | A |  | YES | A | YES | A | YES | A | YES
5.3 | Barometric Pressure |  |  |  | bara | 0.914~0.991 | 0.991 |  | YES | A | YES | A | YES | A | YES
6 | OIL FREE SCREW COMPRESSOR
6.1 | Quantity |  |  |  |  | 1 | A |  | YES | A | YES | A | YES | A | YES
6.2 | Manufacturer |  |  |  | - | VTS | HAVAYAR |  | YES | HAVASAN- AirEnd GHHRAND | YES | GHH RAND | YES | GHH | YES
6.3 | Compressor Allowable Operating Temperature (Max. / Min.) |  |  |  | °C | 5/50 | A |  | YES | A | YES | A | YES | A | YES
6.4 | Delivered Flow |  |  |  | Nm³/hr | VTS | 194 |  | YES | 438 @ Site | YES | FAD=320 m3/hr | YES | 124 | YES
6.5 | Design Pressure |  |  |  | barg | 12.5 | A |  | YES | A | YES | A | YES | A | YES
6.6 | Package Outlet Air Pressure |  |  |  | barg | 9 | 9.5 |  | YES | A | YES | A | YES | A | YES
6.7 | Max. Outlet Air temperature @ after cooler outlet |  |  |  | °C | 65 | 60 |  | NO | A | YES | A | YES | A | YES
6.8 | Max Dust Particle Size |  |  |  | - | ≤ 0.1 µm | A |  | YES | A | YES | A | YES | A | YES
6.9 | Noise Level |  |  |  | dB(A) | 85 | A |  | YES | A | YES | A | YES | A | YES
6.1 | Capacity Control Method |  |  |  | - | Load/Unload | A |  | YES | A | YES | A | YES | A | YES
6.11 | Cooling Type |  |  |  | - | Air Cooled | A |  | YES | A | YES | A | YES | A | YES
6.12 | Intake Filter |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
6.13 | Air-end Manufacturer / Model |  |  |  | - | VTS | GHH Rand/CD8D |  | YES | AirEnd GHHRAND - CD 8D | YES | GHH Rand/CD8D | YES | GHH | YES
6.14 | Power Transmission Method |  |  |  | - | Direct Coupled or Gear Type | Gear Type |  | YES | Gear Type | YES | Direct Coupled | YES | Direct Coupled | YES
6.15 | Weight |  |  |  | kg | VTS | 1817 |  | YES | 1900 | YES | NS | NO | according catalogue data for compressor and dryer | YES
6.16 | Dimension (L x W x H) |  |  |  | mm | VTS | 2240 x 1370 x 1985 |  | YES | 1999 x 1200 x 1650 | YES | 2450x1300x1950 | YES | according catalogue data for compressor and dryer | YES
6.17 | Enclosure Fan Motor Power / Qty |  |  |  | kW | VTS | 5.5/1 |  | YES | 4 | YES | 75 | YES | 3KW/1 | YES
6.18 | Controller of Compressor Skid |  |  |  | - | PLC | A By N2 package UCP |  | YES | A BY N2 PACKAGE UCP | YES | TYPE C, QTY=1 | YES | PLC | YES
6.19 | Control Panel Power |  |  |  | KW | VTS | 64.5kW (as per havayar load list) |  | YES | NS | NO | NS | YES | 110VAC/230VAC | YES
6.20 | Out Put Serial Link |  |  |  | - | VTS | Via hardwired |  | NO | NS | NO | NS | NO | MODBUS | YES
7 | MAIN MOTOR
7.1 | Manufacturer |  |  |  | - | VTS | JEMCO |  | YES | WEG | YES | JEMCO/OME | YES | ABB/SIEMENS/WEG | YES
7.2 | Motor Power |  |  |  | kW | VTS | 55 |  | YES | 55 | YES | 75 | YES | 45 | YES
7.3 | Power Supply |  |  |  | V / HZ / PH | 400/50/3 | A |  | YES | A | YES | A | YES | 400/50/3 | YES
7.4 | IP Degree / Temperature Class |  |  |  | - | VTS | 55/B |  | YES | IP 55 Insulation Class=F- Motor Temp. Rise Class: B | YES | 55/T3 | YES | 55/T4 | YES
7.5 | Speed, Motor / Compressor |  |  |  | rpm | VTS | 3000 |  | YES | 3000 | YES | 2950 | YES | 30000 | YES
8 | PROCESS DESIGN
8.1 | Dry Air Demand for Nitrogen Production (at inlet to N2 Generators) |  |  |  | Nm3/hr | VTS | 165 |  | YES | 206.5 | YES | 188 | YES | 181 | YES
8.2 | N2 Outlet Operating Pressure |  |  |  | barg | 8.5 | 8 |  | NO | 6.5 | YES | A | YES | 8.5 | YES
8.3 | N2 Package Pressure Drop |  |  |  | barg | max. 1 bar | A |  | YES | A | YES | A | YES | A | YES
8.4 | Design Pressure |  |  |  | barg | 12.5 | A |  | YES | A | YES | A | YES | A | YES
8.5 | Dew Point |  |  |  | °C | -70 @ 1.013 bara | A |  | YES | A | YES | A | YES | A | YES
8.6 | Max Oil Content- Inlet |  |  |  | - | ≤ 1 ppm wt | NA |  | YES | NA | YES | A | YES | A | YES
8.7 | Max Oil Content- Outlet |  |  |  | - | Oil Free | A |  | YES | A | YES | A | YES | A | YES
8.8 | Max Allowable Dust |  |  |  | Micron | Less than 3 | A |  | YES | A | YES | A | YES | A | YES
8.9 | Nitrogen Purity |  |  |  | % vol | 99.9 | A |  | YES | A | YES | A | YES | 99 | NO
8.10 | Oxygen Content |  |  |  | % vol | 0.1 (max) | A |  | YES | A | YES | A | YES | 0.5(MAX) | NO
9 | AIR DRYER
9.1 | Manufacturer |  |  |  | - | VTS | HAVAYAR |  | YES | Omega Air | NO | PARS COMPRESSOR | YES | ASA CO | YES
9.2 | Type / Design Code |  |  |  | - | Heatless Desiccant/ASME SEC. VIII DIV.1 & 2 | Heatless Desiccant/ASME SEC. VIII DIV.1 |  | YES | Heatless Regeneration Adsorb Dryer/ASME SEC. VIII DIV.1-API code vesseles | YES | A | YES | A | YES
9.3 | Dryer Life Time |  |  |  | - | not less than 3 years | 3~5 |  | YES | NS | NO | A | YES | A | YES
9.4 | Quantity |  |  |  | - | 1 | A |  | YES | A | YES | A | YES | A | YES
9.5 | Desiccant Material |  |  |  | - | Molecular seive /Activated Alumina | A |  | YES | A | YES | A | YES | Molecular seive | YES
9.6 | Cycle time |  |  |  | min | VTS | 7~15 |  | YES | NS | NO | 20 | YES | 2002-05-03 | YES
9.7 | Dryer Design Capacity |  |  |  | Nm³/hr | 34 | A |  | YES | 1204 m3/hr | YES | 420 | YES | 34 | YES
9.8 | Inlet Flow Rate |  |  |  | Nm³/hr | VTS | 194 |  | YES | 438 | YES | 225 | YES | 110 | YES
9.9 | Outlet Flow Rate |  |  |  | Nm³/hr | 124 | 165 |  | YES | 1204 m3/hr | YES | 188 | YES | 124 | YES
9.10 | Inlet Temperature |  |  |  | °C | 60 | 30 |  | NO | 55 | NO | A | YES | 60 | YES
9.11 | Hydrotest Pressure |  |  |  | barg | VTS (1.5*MAWP) | 1.3 * Design pressure |  | YES | A | YES | A | YES | A | YES
9.12 | Regeneration Flow Ratio |  |  |  | % | VTS | 15 |  | YES | NS | NO | 15.2 | YES | 15 | YES
9.13 | Dew Point |  |  |  | °C | -40 @ 8 barg | A |  | YES | NS | NO | A | YES | A | YES
9.14 | Oprating Pressure |  |  |  | barg | 9 | A |  | YES | NS | NO | A | YES | A | YES
9.15 | Design Pressure |  |  |  | barg | 12.5 | A |  | YES | A | YES | A | YES | A | YES
9.16 | Tower Design Code |  |  |  | - | ASME SEC. VIII DIV.1 | A |  | YES | A | YES | A | YES | A | YES
9.17 | Material for Shell / Head |  |  |  | - | VTS | SA106 Gr B/SA 234 WPB |  | YES | SA106 Gr 70/A106 | YES | CS | YES | A516 Gr. 70 | YES
9.18 | Corrosion Allowance |  |  |  | mm | 3.2 | A |  | YES | A | YES | A | YES | A | YES
9.19 | Safety Valve |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
9.20 | Pre Filter / Qty. |  |  |  | - | Required / 2 | A |  | YES | NS | NO | A | YES | A/2 | YES
9.21 | After Filter/ Qty. |  |  |  | - | Required / 2 | A |  | YES | NS | NO | A | YES | A/2 | YES
9.22 | Filter Manufacturer |  |  |  | - | VTS | HAVAYAR |  | YES | NS | NO | MIKROPOR | NO | Dominic hunter | YES
9.23 | Dryer LCP |  |  |  | - | Yes , IP65 | Yes , IP65 (LCP include only stop, start and status without control function) |  | YES | A | YES | A | YES | Yes , IP54 | YES
9.24 | Dryer instrumentation/IP/EEX |  |  |  | - | As per Specification | IP65, Safe (Non-Ex) |  | YES | NS | NO | A | YES | According PID/54/safe location | YES
9.25 | Cabling to LCP |  |  |  |  | Required as per specification | A: (ON SKID UP TO JB/LCP IS BY HAVAYAR) |  | YES | N | NO | A (Withim BL) | YES | A | YES
9.26 | Dryer Controller Type |  |  |  | - | Microprocessor | By N2 package UCP |  | YES | A | YES | A | YES | PLC | YES
10 | NITROGEN GENERATOR
10.1 | Type of Nitrogen Generator |  |  |  | - | PSA | A |  | YES | A | YES | A | YES | A | YES
10.2 | Quantity |  |  |  | - | 1 | A |  | YES | A | YES | A | YES | A | YES
10.3 | Manufacturer |  |  |  | - | VTS | HAVAYAR |  | YES | OMEGA AIR | NO | PARS COMPRESSOR | YES | ASA CO | YES
10.4 | Design Code |  |  |  | - | ASME Sec. VIII, Div. 1 & 2 | A |  | YES | N | NO | A | YES | A | YES
10.5 | Adsorption Material | Adsorption Material | Adsorption Material | Adsorption Material | - | VTS | Carbon Molecularseive |  | YES | Carbon molecular sieve (CMS) | YES | CMS | YES | Carbon Molecular seive | YES
10.6 | Adsorption Life Time |  |  |  | - | Not less than 3 Years | A |  | YES | A | YES | A | YES | 1 YEARS | NO
10.7 | Adsorber Vessel Material | Adsorber Vessel Material | Adsorber Vessel Material | Adsorber Vessel Material | - | VTS | SA106 Gr B/SA 234 WPB |  | YES | Carbos steel | YES | NS | YES | A516 Gr. 70 | YES
10.8 | Maximum Allowable Inlet Temperature | Maximum Allowable Inlet Temperature | Maximum Allowable Inlet Temperature | Maximum Allowable Inlet Temperature | °C | VTS | 30 |  | YES | 55 | YES | 35 | YES | 55 | YES
10.9 | Volume of One Adsorber | Volume of One Adsorber | Volume of One Adsorber | Volume of One Adsorber | m3 | VTS | After P.O. |  | YES | 305 lit | YES | After P.O. | YES | After P.O | YES
10.10 | Design Flow / Regeneration Flow |  |  |  | Nm3/hr | 34 / VTS | 34 |  | YES | 35.15 | YES | After P.O. | YES | 34/60 | YES
10.11 | Regeneration Sequence Duration |  |  |  | Sec | VTS | After P.O. |  | YES | A (Pressure Swing Adsorption (PSA)) | YES | After P.O. | YES | 5/3/2 | YES
10.12 | Room Mounted Control Panel |  |  |  | - | PLC Type C | PLC S7-1200 |  | NO | NS | N | PLC-Type C | YES | PLC TYPE C | YES
10.13 | SIL Rated loops for safety functions |  |  |  |  | Required | NA |  | NO | NS | N | To be Gudied by SIL meeting | YES | A | YES
10.14 | Control Panel Power ( UPS/Non UPS) |  |  |  | KW | 110VAC/230VAC | 2kW/1.5kW (Included in N2 package UCP) |  | YES | NS | N | A | YES | A | YES
10.15 | Instrumentation/Analyzer |  |  |  |  | As per Specification | A (deviation check) |  | YES | A (oxygen analyzer) | ?? | A (O2/N2 Analyzer) | YES | A | YES
10.16 | Local Control Panel |  |  |  |  | Required per compresssor | LCP include only stop, start and status without control function. Control is by N2 package UCP |  | YES | A | YES | A | YES | A | YES
10.17 | Cabling to LCP |  |  |  |  | Required | A ON SKID UP TO JB/LCP IS HAVAYAR |  | YES | N | YES | A: Withim BL | YES | A | YES
10.18 | Serial Link connection |  |  |  | - | Modbus RTU | A (N2 package UCP) |  | YES | NS | NO | A | YES | A | YES
10.19 | Exhaust Silencer SPL @ 1 m distance |  |  |  | dB (A) | < 85 | A |  | YES | A | YES | A | YES | A | YES
10.20 | Corrosion Allowance |  |  |  | mm | 3.2 | A |  | YES | Manufacture STD | NO | A | YES | A | YES
10.21 | Oxygen analyzer and moisture analyzer |  |  |  | - | Required | A |  | YES | A | YES | A (O2 analyzer at n2 outlet and dew point tansmitter at Air dryer outlet) | YES | A | YES
10.22 | Relief valves |  |  |  | - | Required | A |  | YES | A | YES | A | YES | A | YES
10.23 | PSA Unit Skid Weight |  |  |  | kg | VTS | 820 |  | YES | 1215 | YES | NS | NO | ACCORDING TO CATALOGUR OF NITROGEN GENERATOR | YES
10.24 | Dimension (L X W X H) |  |  |  | mm | VTS | 110x860x2154 |  | YES | 1749 x 860 x 2361 | YES | NS | NO | ACCORDING TO CATALOGUR OF NITROGEN GENERATOR | YES
11 | Chillers / Heat Exchangers or Refrigerant Dryer
11.1 | Manufacturer / Model | Manufacturer / Model | Manufacturer / Model | Manufacturer / Model | - | VTS | As per Havayar sub vendor list/after P.O. |  | YES | OMEGA AIR-RDP 1300 | YES | After P.O. | YES | NA | YES
11.2 | Cooling Medium | Cooling Medium | Cooling Medium | Cooling Medium | - | VTS | AIR |  | YES | Air cooled | YES | Refrigerant R410a/Water | YES |  | YES
11.3 | Inlet Temperature (Operating) | Inlet Temperature (Operating) | Inlet Temperature (Operating) | Inlet Temperature (Operating) | °C | VTS | 60 |  | YES | 55 | YES | NS | NO |  | YES
11.4 | Outlet Temperature (Operating) | Outlet Temperature (Operating) | Outlet Temperature (Operating) | Outlet Temperature (Operating) | °C | VTS | 30 |  | YES | 45 | YES | NS | NO |  | YES
11.5 | Design Temperature | Design Temperature | Design Temperature | Design Temperature | °C | VTS | 85 |  | YES | 85 | YES | NS | NO |  | YES
11.6 | Operating Pressure | Operating Pressure | Operating Pressure | Operating Pressure | barg | VTS | 9.5 |  | YES | 10 | YES | NS | NO |  | YES
11.7 | Heat Exchanger Duty | Heat Exchanger Duty | Heat Exchanger Duty | Heat Exchanger Duty | KW | VTS | 5 |  | YES | 10.6 kw heat reject | YES | 4 | YES |  | YES
12 | PRE FILTER
12.1 | Manufacturer / Model | Manufacturer / Model | Manufacturer / Model | Manufacturer / Model | - | VTS | HAVAYAR/OMEGA / HFR 0186 |  | YES | NS | NO | MIKROPOR | NO | Dominic hunter | NO
12.2 | Volume | Volume | Volume | Volume | Lit | VTS | After P.O. |  | YES | NS | NO | After P.O. | YES | 1/2 inch AO TYPE | YES
12.3 | Casing Material | Casing Material | Casing Material | Casing Material | - | VTS | SA106 Gr B/SA 234 WPB |  | YES | NS | NO | CS | YES | C.S. | YES
12.4 | Filter Cartridge Material | Filter Cartridge Material | Filter Cartridge Material | Filter Cartridge Material | - | VTS | borosilicate micro fibres |  | YES | NS | NO | SS/PEEK | YES | fiberglass | YES
12.5 | Maximum Working Pressure | Maximium Woking Pressure | Maximium Woking Pressure | Maximium Woking Pressure | barg | VTS | 9.5 |  | YES | NS | NO | NS | NO | 16 | YES
12.6 | Maximum Working Temperature | Maximum Working Temperature | Maximum Working Temperature | Maximum Working Temperature | °C | VTS | 30 |  | YES | NS | NO | NS | NO | 66 | YES
12.7 | Filtration Mesh | Filtration Mesh | Filtration Mesh | Filtration Mesh | Micron | VTS | 1 |  | YES | NS | NO | 0.1 | YES | 0.1 | YES
12.8 | Residual Oil Content After Filtration | Residual Oil Content After Filtraton | Residual Oil Content After Filtraton | Residual Oil Content After Filtraton | mg/m3 | VTS | OIL FREE |  | YES | NS | NO | NS | NO | 0.1 | YES
13 | AFTER FILTER
13.1 | Type / Manufacturer / Model | Type / Manufacturer / Model | Type / Manufacturer / Model | Type / Manufacturer / Model | - | Dust filter | HAVAYAR/OMEGA / HFR 0186 |  | YES | OMEGA AIR- AF 0476-R | NO | Dust | YES | Dominic hunter | NO
13.2 | Volume | Volume | Volume | Volume | Lit | VTS | After P.O. |  | YES | 2.8 Lit. 510 Nm3/hr | YES | NS | NO | 1/2 inch AA TYPE | YES
13.3 | Casing Material | Casing Material | Casing Material | Casing Material | - | VTS | SA106 Gr B/SA 234 WPB |  | YES | AL | YES | CS | YES | C.S. | YES
13.4 | Filter Cartridge Material | Filter Cartridge Material | Filter Cartridge Material | Filter Cartridge Material | - | VTS | borosilicate micro fibres |  | YES | 32075 R borosilicate micro fibres | YES | SS | YES | fiberglass | YES
13.5 | Maximum Working Pressure | Maximium Woking Pressure | Maximium Woking Pressure | Maximium Woking Pressure | barg | VTS | 9.5 |  | YES | 16 | YES | NS | NO | 16 | YES
13.6 | Maximum Working Temperature | Maximum Working Temperature | Maximum Working Temperature | Maximum Working Temperature | °C | VTS | 30 |  | YES | 65 | YES | NS | NO | 66 | YES
13.7 | Filtration Mesh |  |  |  | µm | VTS | 0.1 |  | YES | 1 | YES | 5 | YES | 0.01 | YES
13.8 | Residual Oil Content After Filtration |  |  |  | mg/m3 | VTS | OIL FREE |  | YES | OIL FREE | YES | Oil Free | YES | 0.1 | YES
14 | AIR RECEIVER VESSEL | [14 empty] | `
14.1 | Design Code |  |  |  | - | ASME SEC. VIII DIV. 1 & 2 | ASME SEC. VIII DIV. 1 |  | YES | ASME SEC. VIII DIV. 1 | YES | A | YES | A | YES
14.2 | Quantity |  |  |  | - | VTS | 1 |  | YES | 1 | YES | 1 | YES | 1 | YES
14.3 | Capacity |  |  |  | m³ | VTS | 1 |  | YES | 10 | YES | NS | NO | 3 | YES
14.4 | Position (Vertical/Horizontal) |  |  |  | - | VTS | Vertical |  | YES | Vertical | YES | V | YES | VERTICAL | YES
14.5 | Dimensions (L x TL/TL) |  |  |  | mm | VTS | 850x1600 |  | YES | ID= 1700 , TL/TL=3850 | YES | After P.O. | YES | 1500*1500 | YES
14.6 | Design Pressure |  |  |  | bar g | VTS | 12.5 |  | YES | 12.5 | YES | NS | NO | 16 | YES
14.7 | Hydrotest Pressure |  |  |  | bar g | VTS (1.5*MAWP) | 1.3*Design pressure |  | YES | 16.25 | YES | A | YES | 24 | YES
14.8 | Material |  |  |  | - | VTS | SA 516 GR 70 |  | YES | SA 516 Gr.70 | YES | CS | YES | A516 GR.70 | YES
14.9 | Corrosion Allowance |  |  |  | mm | VTS | 3.2 |  | YES | 3.2 | YES | 1.6 | YES | 3.2 | YES
15 | N2 BUFFER VESSEL
15.1 | Design Code |  |  |  | - | ASME SEC. VIII DIV. 1 & 2 | ASME SEC. VIII DIV. 1 |  | YES | ASME SEC. VIII, DIV.I | YES | A | YES | A | YES
15.2 | Quantity |  |  |  | - | VTS | 1 |  | YES | 1 | YES | 1 | YES | 1 | YES
15.3 | Capacity |  |  |  | m³ | VTS | 1 |  | YES | 10 | YES | After P.O. | YES | 1 | YES
15.4 | Position (Vertical/Horizontal) |  |  |  | - | VTS | Vertical |  | YES | Vertical | YES | V | YES | VERTICAL | YES
15.5 | Dimensions (L x TL/TL) |  |  |  | mm | VTS | 850x1600 |  | YES | ID= 1700 , TL/TL=3850 | YES | NS | NO | 900*1500 | YES
15.6 | Design Pressure |  |  |  | bar g | VTS | 12.5 |  | YES | 12.5 | YES | NS | NO | 16 | YES
15.7 | Material |  |  |  | - | VTS | 1.3*Design pressure |  | NO | SA 516 Gr.70 | YES | CS | YES | A516 GR.70 | YES
15.8 | Corrosion Allowance |  |  |  | mm | VTS | 3.2 |  | YES | 3.2 | YES | 1.6 | YES | 3.2 | YES
FINAL CONCLUSION | [6 empty] | ACCEPTED |  |  | CONDITIONALLY ACCEPTED(if approved by the CLIENT) |  | ACCEPTED |  | ACCEPTED
NOTES:
ABBREVIATIONS: A: ACCEPTED By Vendor N: NOT ACCEPTED By Vendor NA:Not Applicable NS:Not Specified C:Clarification Required VTS: Vendor to Specify