| # | Clarification Title | Clarification Description (Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- | --- |
| GENERAL |  |  |  |  |  |
|  | Documents Priority | Vendor to confirm that in case of contradiction between this TCL and offer; vendor confirmation of compliance through this technical clarification is governed and shall be followed by vendor after order. In such case offer won’t be considered as basis of any claim after order. | Noted. | Closed |  |
|  | Deviation List | Bidder shall confirm his full compliance to meet all purchaser documents listed and attached to MR, code / standards listed in MR with ref. No. "BK-GCS-PEDCO-120-ME-MR-0008" as well as MR requirements. All deviations shall be listed in project deviation form, attach to this TCL, signed and stamped. Notes: 1-Any exception and deviation from the requirements of MR and the related specifications including referenced codes & standards shall be clearly declared by vendor in writing for purchaser’s approval at bid stage by using of the format included in “Letter Of Conformity” attached to material requisition. Raising no deviation to any single requirement means full compliance of vendor quotation to that requirement. Purchaser has no responsibility to discover deviations or alternatives scattered over the proposal in addition to what proclaimed explicitly in deviation list; hence such deviation (if any) is disregarded and shall not be considered for vendor claim in future. (Vendor to confirm) 2- Bidder shall confirm that all MR attachments listed in MR are available for her for review at bid stage. 3-Considering items 1 & 2, please note that any deviation at detail stage will not be accepted by purchaser. | Noted. | Closed |  |
|  | Documents Priority | Bidder to confirm his compliance with documents priority stated in MR. Any conflict between the documents shall be notified by bidder to purchaser and resolved by his agreement | Noted. | Closed |  |
|  | Requirement For Documents | Bidder to confirm that documents required after purchase order shall be submitted in accordance with “Vendor documents min. requirement list” attached to the MR. | Noted. | Closed |  |
|  | Documents | Bidder shall provide following documents while bidding: 1- Copy of valid quality system certificate(ISO 9001/2 or 3) 2- Sub- vendors / sub-suppliers list. 3- Deviation list with letter of conformity (Refer to item A2 above) 4- Reference and Experience List 5- Joint venture agreement (If any) with any company to design / fabrication of equipment. In case of joint venture ; qualified documents of the company who is part of joint venture shall be also submitted | Noted. | Closed |  |
|  | Sub-vendors | Bidder to confirm that Sub-Vendors shall be selected from Project’s AVL. Please refer to purchaser’s comments on vendor’s sub-vendors list. |  | Bidder to confirm that Sub-Vendors shall be selected from Project’s AVL. Please refer to purchaser’s comments on vendor’s sub-vendors list. |  |
|  | Painting specification | Bidder to confirm that surface preparation and painting of all equipment material including valves , pipes , fittings and everything within the package are in accordance with project painting specification with ref. "BK-GNRAL-PEDCO-000-PI-SP-0006" attached to MR. | Noted. | Closed |  |
|  | Specification | Bidder to confirm that Packing, Marking, Preservation and Preparation for Shipment will be done in accordance to the project specification with Doc. No; BK-GNRAL-PEDCO-000-QC-PR-0045 attached to the MR. | Packing procedure has been considered for each equipment separately (for example vessel, pump, instrument, piping, etc.) but all equipment in this project will be shipped inside the package except of instrument that is located on wooden box. There is no clearly packing type for skid mounted package. We considered bubble wrape and selefon tape. Please confirm or describe exactly packing type. | Noted, vendor shall be followed specification with Doc. No; BK-GNRAL-PEDCO-000-QC-PR-0045 |  |
|  | Inspection and Test Plan | Inspection and Test Plan / Quality Control Plan and their related inspection level (Witness, Hold, Review and Approval) shall be at least in accordance with MR and all project requirement such as NDT PROCEDURE. Any deviation is not accepted unless otherwise specified in deviation list and approved by Purchaser. | Noted. | Closed |  |
|  | Material Certificate | Bidder to confirm that for all pressure parts and those required special consideration or stainless steel as well as for supports the material certificate should be in accordance with EN 10204, 3.1 Material certificate for non-pressure parts shall be in accordance with EN 10204, 2.2 | Noted. | Closed |  |
|  | Scope | Bidder shall confirm the scope of work and supply are fully in accordance with MR and its attachment with considering following items: 1- The consequences of HAZOP and SIL study shall be in vendor scope of supply and work. 2- Participation in technical meeting whenever it is necessary by Purchaser/Client to close engineering document after order is in vendor scope 3- Lifting beams ( Spreader beams) for erection with sling shackle and etc shall be designed and supplied by vendor 4- N2 preservation with pressure regulator, valve & flexible hoses during transportation & 18 months of site storage based on requirements in MR shall be in vendor scope of supply / work. 5- All utility conditions shall be as per document "Basic engineering design data (10‐BD‐00‐PR‐SPC‐0001)". Moreover, bidder shall consider utility noted condition as per project design data. If other utility condition is needed, whole required facilities is in vendor scope of work/supply. 6- Anchor bolts | - Noted. - Noted. - There is no needed. - Corrosion inhibitor is not needed N2 for Blanketing and material of tank is Stainless steel therefore N2 Preservation for Shipping and storing is not needed. Please clarify. - Noted. - Noted. | Noted and closed |  |
|  | Applied standard | Applied Standards for equipment design, fabrication and test shall be listed | Noted. | Closed |  |
|  | outdoor installation/ operation under project site conditions | Vendor shall confirm Air Compressor Packages, Dryer Packages and N2 generation package are fully suitable for outdoor installation/operation under project site conditions “Process Basis of Design; BK-GNRAL-PEDCO-000-PR-DB-0001 “without requiring any additional protection. | These items are out of vendor scope and there is not needed based on chemical injection package PID. Please clarify. | Closed |  |
|  | Suitability of utility characteristics available at site | Vendor shall confirm suitability of utility characteristics available at site as per project site conditions “Process Basis of Design; BK-GNRAL-PEDCO-000-PR-DB-0001 “. Supplying all facility for utility distribution and regulation shall be part of the vendor scope. | Noted. | Closed |  |
|  | Warranty | Vendor shall warranty the engineering, materials and workmanship of the equipment/goods. Under this warranty, all materials, parts, and assemblies found to be defective during the guarantee period shall be replaced free of charge by VENDOR. Also, The guarantee period shall be eighteen (18) months from the date of delivery or twelve (12) months from the installation date of each equipment/packages at site. | Noted. | Closed |  |
|  | Document | Bidder to confirm that all native files due to all calculations and drawings shall be submitted for purchaser approval after order. | Noted. | Closed |  |
|  | Project’s MR | Vendor shall follow project’s MR (Updated Revision D01 with Attachments) as Attachment#1 of this TCL. | MR rev D01 has been considered. | Vendor shall follow project’s MR (Updated last revision with Attachments) as Attachment#1 of this TCL |  |
| PROCESS |  |  |  |  |  |
|  | Process Data | 1- inhibitor injection rates (Pint/MMSCF) shall be specified 2- Solvent specification shall be specified 3- The ratio of solvent to inhibitor shall be specified 4- All Equipment shall be designed as per project design criteria | - Inhibitor Dosing Range has been specified 2.27 lit/h as per PID and process duty specification in vendor package datasheet. Required injection must be specified by chemical vendor. - Solvent specification must be specified by chemical vendor. - Ratio of solvent to inhibitor must be specified by chemical vendor. - Noted. |  |  |
|  | Project documents | Latest revision of process documents shall be followed by vendor as Attachment#2 of this TCL. | attachment is not found. | Latest revision of process documents shall be followed by vendor as Attachment#2 of this TCL. |  |
| MECHANIC |  |  |  |  |  |
|  | Document Requirement | Bidder to submit all required documents with tender as per “VDR Form” in the MR. For example below documents: 1-Marked up and Filled out MR scope of supply and works (It shall be signed and stamped) 2-GAD for air compressors, air dryers and nitrogen generators with dimensions, all auxiliaries and heaviest part weight table (by considering air cooler in the package) 3-Cross sectional drawing for compressors with BOM 4-Performance Curves 5-Equipment data sheet in each standard format 6-Utility consumption and load list 7-Spare part list 8-Special tool list 9-P&ID’s dedicated for air compressor, dryer and nitrogen generation packages with all equipment, instruments and lube oil, cooling and control systems. 10-Noise Data 11-Equipment List on detail for mechanical and other items | - Noted. - Not applicable for this package. - Not applicable for this package/ - Not applicable for this package - Package datasheet has been issued. Standard datasheet will be issued after PO. - Utility consumption is not applicable and load list Will be issued after PO - Has been issued. - There is no special tools. - PID endorsement will be issued. - Project requirement will be considered (<85dBA @ 1m) - Will be issued after PO. | - Marked up and Filled out MR scope of supply and works (It shall be signed and stamped) - GAD for chemical injection package, all auxiliaries and heaviest part weight table. - Cross sectional drawing pumps with BOM - Performance Curves. - Noted - Utility consumption list and load list shall be issued BY VENDOR after P.O - Noted - Not accepted - Noted - Noted - Noted |  |
|  | Ladder and platforms | Access ladder and platforms, stairway shall be studied, designed and supplied by vendor. Relevant detail drawings shall be submitted for approval. They shall comply with project standards attached to MR, as minimum. | Ladder will be considered for tank and there is no needed platform because tank is flat head. | Noted and closed |  |
|  | Interconnecting piping | Design and supply of all interconnecting piping between equipment and all instruments, valves and … on them is in the vendor's scope. Also all between skid piping (including supporting) c/w all instrument and valve on them shall be designed, prefabricated and supplied by vendor. Detailed isometric DWGs shall be submitted for them. Note1: On skid piping to be assembled at vendor's shop. Note2; Outside skid piping to be prefabricated and match marked for site assembling. | Requirement for piping and interconnection piping inside the package is in vendor scope of work. Isometric drawing for package with ½” Tubing is not applicable. | Noted and closed |  |
|  | Heat tracing c/w supports, clips and etc. | Design and supply of heat tracing c/w supports, clips, and other provisions (including panels, heating cables and relevant connectors, electrical cables, junction boxes and thermostats) shall be part of the vendor scope. | There is not specified heat tracing for this package please clarify. | Noted and closed |  |
|  | Insulation c/w supports, clips and etc. | Design and supply of insulation c/w supports, clips and other provisions shall be part of the vendor scope. | There is not specified heat tracing for this package please clarify. | Noted and Closed |  |
|  | Commissioning spare parts | Pre-commissioning, commissioning and start up spare parts shall be supplied by vendor. Vendor shall confirm to provide all required spare parts as per project spare part list attached to MR. | Noted. | Noted and Closed |  |
|  | Two years spare parts | Two years spare parts shall be submitted by vendor as per project spare part list attached to MR. | Noted. | Noted and Closed |  |
|  | Capital spare part | Capital spare part shall be submitted by vendor as optional offer. | There is not needed. | Noted and Closed |  |
|  | Vent and Drain of Packages | All vents and drains of the packages to be valved, manifolded and to be routed to the edge of skid. | Valve will be considered for all drains but there is not needed valve for vent. | Noted and Closed |  |
|  | Tie-in | All Tie-in for equipment in the packages shall be equipped will flange and valves | According to PID flange will be considered there is not needed Valve because each line has separate isolating valve. | Noted and Closed |  |
|  | PMI, pickling and passivation | Positive material identification (PMI), pickling and passivation for non-carbon steel material to be included in vendor’s scope of work. | Noted. | Closed |  |
|  | Coupling | Couplings and coupling to shaft junctures shall be rated for at least the maximum driver horsepower plus minimum service factor of 1.5. | All service factors for dosing pumps will be considered based on API 675. | Closed |  |
|  | Skid of the packages | 1-Vendor shall specify number of skids inside package with dimension and weight and preliminary general arrangement. 2-In case of multi skid, please clarify if there is any special procedure for installing and assembling of loose parts. 3-Each skid shall be furnished with 4-point lifting facility and no. two earth lugs located at opposite sides and nameplate made of SS material. 4-Vendor shall specify space required around the skid for maintenance. | - We have one package and one skid. Sample GAD will be attached. - We have one skid - Noted. - We have one skid. | - Noted - Noted - Noted - Noted |  |
|  | Noise level | If noise enclosure will be required for meeting the project noise limit, it shall be supplied by vendor. Any required facilities for ventilation, fire and gas detection and fire extenuation (if any) for enclosure shall be supplied by vendor. | There is not needed extra facilities for this package. | Closed |  |
|  | Material | Below requirements shall be followed by vendor: -Wall/roof Plates of tank(s) shall have a minimum thickness of 5 mm. Plates material shall be stainless steel type 316L. -Material of the Storage Tank(s) and its leg supports shall be S.S 316L -The pumps shall be constructed of 316L stainless steel with components suitable for the specified chemical duty. The material grades shall be as per API 675. -All wetted parts of mixers shall be stainless steel 316L. - The minimum size of the package pipes shall be 3/4” and material used of them shall be S.S316L. - Body material of pulsation dampener to be considered SS316L. -The package material shall be in compliance with the requirements of the project “Corrosion Study & Material Selection Report” and project “Piping Material Specification”. | - noted. - we considered S.S.316L PAD and Carbon Steel Lug. - noted. -noted. -based on flow rate (2.27 lit/h), 3/4 “ piping is very big and is not recommended. We recommend to use ½” tubing as suitable for piping inside the package for best performance and guarantee. - noted. - noted. | -closed -closed -Closed -Closed - Not accepted, Package Pipes size shall be at least 3/4" -Closed |  |
|  | Motor Power | For motor driven units, the motor nameplate rating (exclusive of the service factor) shall be a minimum of 110 % of the maximum power (including coupling losses) required for any of the rated conditions. Vendor shall confirm that motors nominal power has been considered with derating factor of site ambient condition. | Noted. | Closed |  |
|  | Corrosion allowance | For all parts made of carbon steel, corrosion allowance of 3.2 mm at least to be considered by vendor. In addition corrosion allowance shall be in accordance with the project "Corrosion Study & Material Selection Report". This requirement shall be followed by vendor. | Noted. | Closed |  |
|  | Pump’s Capacity | Capacity required for high and low pressure pumps of package is 2.21 and 3.08 lit/hr respectively. As per API 675 standard, Rated capacity shall be at least 110% of maximum capacity required. This requirement to be followed by vendor and revised his offer accordingly. | Noted. | Closed |  |
|  | Mixer | - Mixers shall be stable while agitating contents of Tank from 1/3 to full. - Mixer sealing type shall be mechanical seal. - Vendor shall follow all requirements of IPS-M-PM-330(1) standard for mixer. | - Noted. - Tank is atmospheric and mixer will be located on top of tank therefore sealing for this type of mixer is not applicable. - Noted. | - Closed - suitable Packing shall be supplied by vendor. - Closed |  |
|  | Pump’s MAWP | Maximum allowable working pressure for pumps to be submitted by vendor in next revision of technical offer. | Maximum pump pressure has been specified in datasheet. | MAWP( Maximum allowable working pressure for pumps to be submitted by vendor in next revision of technical offer. |  |
|  | Pulsation damper | Pulsation dampeners shall be provided by vendor to limit pulsation within ±3%. | Noted. | Closed |  |
|  | Applied Standards | Applied Standards for equipment design, fabrication and test shall be listed. -The controlled volume pump shall meet the requirements of API 675 as amended and supplemented by IPS-M-PM-150. -The pulsation dampener and storage tanks shall be designed as per ASME Section Vlll Div. I | - noted. - noted. PVELITE will be considered for design of tank with design pressure ATM+Full of Water. | Noted |  |
|  | Vendor’s Scope | All vents and drains of the package to be valved, manifolded and to be routed to the edge of skid. | All Tie in inside the package is Flange type and routed to edge of skid but all valves will be considered based on endorsement PID. | Noted and closed |  |
|  | Inspection and Test | Test procedures and acceptance criteria will be checked after order with project specifications and related standards. Vendor to confirm to follow project standard and spec. | Noted. | ITP will be finalized during PIM |  |
|  | Purchaser’s approval | Regarding technical offer, diameter, dimension and thickness of each equipment will be checked after receiving vendor calculation and data after order and comments in detail shall be followed without cost impact. | Noted. | Closed |  |
|  | Guarantee | Performance, Process and Mechanical Guarantee shall be in the vendor's scope. | Noted. | Closed |  |
|  | Project’s MR | Vendor shall follow Project’s MR with its Attachments as Attachment#1 of this TCL. (Updated Revision D01 and attachments will be sent for vendor) | There is no attachment to this TCL. | Vendor shall follow project’s MR (Updated last revision with Attachments) as Attachment#1 of this TCL |  |
| MECHANIC FIX |  |  |  |  |  |
| 1. | Fixed equipment mechanical data sheet such as drum /storage tank | Vendor shall submit relevant mechanical data sheet to define shell/head/nozzle/support type & materials & dimension and designing assumption (J.E. / C.A. & etc.…) | Tank is bottom and top flat head. Joint efficiency will be considered based on ASME SEC VIII. Calculation for Top and bottom of tank will be considered based on ROARK Handbook (because tank is not pressurized). Corrosion allowance is zero for S.S.316L. | Noted and closed |  |
| 2. | Special tools | Special tools for lifting of vessel (i.e. spread bar and skirt bracing if required based vendor’s lifting calculation & relevant bolts/nuts/gasket, Hydraulic bolt tensioning device for bolts greater than 1-1/2” and etc ), shall be considered in vendor’s scope. | There is no any special tools for lifting of vessel (tank is very small) and there is no bolt greater than 1 ½”. | Noted and closed |  |
| 3. | Lifting/Shipping | Shipping calculation, hydrotest stability calculation and relevant drawings & temporary shipping support for all equipment shall be considered in vendor’s scope and submitted for purchaser’s review at detail stage. Please confirm | Tank will be shipped inside the package. Tank is very small (1X1.6m) | Noted and closed |  |
| 4. | Spare part for Fix equipment | Commissioning spare part shall be based on vendor recommendation considering followings as the minimum: -Gaskets: 100 % -Internal Gaskets (If required): 100% -Bolts & Nuts, minimum two set: 10% for each size/material/type Two years spare part shall be based on vendor recommendation considering followings as the minimum: -Gaskets: 200 % -Internal Gaskets (If required): 200% -Bolts & Nuts, minimum two set: 10% for each size/material/type installed -Internal Bolting (If required): 10% for each size/material/type installed Please submit priced 2 years spare part list (in SPLIR form and as optional) | Noted. | Closed. |  |
| 5. | preservation | N2 purging preservation with following conditions shall be consider in vendor’s scope of work & supply (it shall be considered in vendor’s base price not as optional): 1-All opening shall be sealed with a suitable metal cover and gasket. Vessels shall be filled with nitrogen gas at a pressure of 0.5 kg/cm2(g). 2-The equipment shall have a temporary gauge to determine purge pressure. 3-Vendor shall submit N2 filling procedure for purchaser/contractor approval at detail stage. 4-All the required ancillaries such as metal covers, bolts & nuts, gaskets and pressure gauge shall be provided by vendor. Please confirm and modify your offer. (using silica gel instead of N2 purge is not acceptable and shall be omit from your offer.) | Tank is S.S.316L therefor there is not needed N2 Purging. | Noted and closed |  |
| 6. | Access for internal loading/unloading | Manhole / hand hole Access for internal loading/unloading of drums to be considered by vendor. | Noted. | closed. |  |
| 7. | Nozzle WRC | Local stress analysis of shells under external loads from piping system and attachments (platforms, pipe supports, davit, lifting lug) shall be included in strength calculation. And also, nozzle load shall be considered according to Allowable Nozzle loads on static Equipment (as per project specification) should be done. Please note that wherever WRC is not applicable FEA shall be done to evaluate local stresses. The original file (native file) of all analysis including all input data and results should be provided by Vendor. Please confirm. | All process nozzles is less than 2” therefore there is not needed to stress analysis. | Noted and closed |  |
| 8. | Loading Data & Anchor Bolt Data | Anchor bolt data (Size, number, B.C.D. ,material ,…) and final loading data including erection, operating and hydro tests shear and moment due to wind and earthquake shall be provided by vendor 1 month after purchase order. Please confirm. | Noted. | Closed. |  |
| 9. | PWHT | When stress relieving is required, whole equipment in one piece without removable internals shall be located in the Furnace. All surfaces of flanges shall be protected by vendor due to prevent of damage. Use of direct flame is not approved. | There is not needed. | Noted and closed |  |
| 10. | Material requirement | Raw materials supplied for Wet H2S service and shall be in strict accordance with NACE standard MR0103, latest edition and project specification attached to MR, shall be followed. Please confirm. | Not applicable for this project. | Noted and closed |  |
| 11. | Project documents | Vendor shall provide compliance with the following project documents: - Specification for pressure vessels [BK-GNRAL-PEDCO-000-ME-SP-0001] - Standard drawing for pressure vessel [BK-GNRAL-PEDCO-000-ME-DW-0001] - Specification for Painting [BK-GNRAL-PEDCO-000-PI-SP-0006] - Specification for insulation [BK-GNRAL-PEDCO-000-PI-SP-0019] - Specification for welding [BK-GNRAL-PEDCO-000-PI-SP-0011] - Mechanical Design Criteria [BK-GNRAL-PEDCO-000-ME-DC-0001] | - Noted. - This document is not existed. - Noted. - This document is not applicable. We have no insulation inside the package. If insulation is required please specified clearly. - Noted. - Noted. | - closed - this document is there on the MR attachments -closed -closed -closed -closed |  |
| 12. | Guarantee | Vendor shall unconditionally guarantee the materials and workmanship on all material and/or services for a period of 12 months after successful start-up at the Purchaser’s Production Site or 18 months after the date of delivery whichever comes earlier. Bidder to confirm. | Noted. | Closed. |  |
| 13. | Material | Manufacturer of FRP vessels is specified as “Tabarestan” in Tank datasheets, while the same is not found in submitted sub-vendor list. Vendor shall revise accordingly. | Tank is S.S.316L in this project. | Closed. |  |
| 14. | Equipment supports | Equipment supports and body local stress analysis at support attachment location shall be performed by Vendor. All required dead/live loading as per project specification shall be considered. Any local increase in body thickness if required due to approved calculation shall be considered by Vendor without any cost impacts. | Noted. | Closed. |  |
| 15. | Seismic/Wind parameters | Vendor shall follow project specifications for Seismic/Wind parameters. Below data shall be considered as minimum requirements: - For seismic: - Code: ASCE 7-10 - Importance Factor: 1. 25 - Site Class: D - Ss = 0.781 - S1 = 1.25 - Fa = 1 - Fv =1.5 - Design wind speed: 120 km/h @10m - Wind Exposure: D - Wind Imp. Factor: 1 | Noted. | Closed. |  |
| 16. | Native Files | Version for all Software to be considered in accordance with code edition. For PV-Elite: PVElite 2019 should be considered for general mechanical calculation. ASME Material Data Base shall be set to 2019. Version of PVElite can be discussed in K.O.M. For Nozzle Pro: Nozzle Pro V8 (PRG2019) For AutoCAD: Native files of drawings to be compatible with AutoCAD 2014. Vendor to confirm. | Noted. | Closed. |  |
| 17. | Accessories | Equipment shall be supplied with all required accessories such as internal parts, nozzles, supports, lifting devices, name plates, earth lugs, insulation supports, fire proofing supports and so on. All internals including vortex breakers are included in the Vendor's scope of supply. |  | Equipment shall be supplied with all required accessories such as internal parts, nozzles, supports, lifting devices, name plates, earth lugs, insulation supports, fire proofing supports and so on. All internals including vortex breakers are included in the Vendor's scope of supply. |  |
| 18. | Attachments | Any attachments which are directly welded internally or externally to the vessel shall be made of the same material grade used for the shell or heads as appropriate. | Noted. | Closed. |  |
| 19. | Minimum Documents | In case of order, the minimum documents which are listed in the table of ATTACHMENT #2 of MR shall be submitted by the Vendor. In addition, if deemed necessary, more specific documents may be required for completion of job and shall be provided by Vendor. | Comment on this document will be issued. | Noted and closed |  |
| 20. | Mechanical Calculation | Vendor shall provide mechanical calculation for all components including pressure parts, non-pressure parts, flat cover (if any), structural parts, etc. as per project specifications. | Will be considered for Tank. | Noted and closed |  |
| 21. | Agitator | The loads originated by the agitator including axial load, torsion & bending moments, to be taken into consideration for check of stresses in the wall of the top head or shell. | Noted. | Noted and closed |  |
| 22. | Detail Drawing | In case of order, complete detail drawing should be provided in separate sheet including but not limited to following list: - General Arrangement - Body detail - Nozzle Detail - External attachment - Internal attachment - Template/Gauge Plate Drawing (for skirt-supported vessels only) - Name Plate - Ladder & platform detail drawing - Development drawing - Transportation Detail Drawing - General Arrangement, complete detail drawings and support drawings related to the removable internals. (if any). All drawings shall be drawn in suitable scale (drawings to be provided in A3 size and shall have weighted part list.) | 1-8. noted. 9. platform is not applicable for flat head tank. 10. tank will be located inside the package therefore there isn’t need this drawing. 11. noted. | Noted and closed |  |
| 23. | Thicknesses after forming | The thicknesses after forming of any pressure retaining parts shall not be less than the calculated thickness (Only positive tolerances on plate thickness are acceptable.) | Noted. | Closed |  |
| 24. | Foundation loading data | Foundation loading data including erection, operating and hydrostatic test, shear and moment due to wind and earthquake shall be provided 1 month after P.O. It’s the Vendor’s responsibility to verify and finalize the quantity/diameter of setting and anchor bolts. | Noted. | Closed |  |
| 25. | Native files | All vendor deliverable shall be submitted with its native files for all revisions. All native e-files should be submitted in original format (e.g. AutoCAD, Word, Excel, etc.) along with PDF file. Vendor to Confirm. | Noted. | Closed |  |
| 26. | Specification for Welded Pressure Vessel | For the vessels which operate under pressure (e.g. with DP: 3.5 barg), project requirements in accordance with Specification for Welded Pressure Vessel: BK-GNRAL-PEDCO-000-ME-SP-0001 shall be fully met by Vendor. Vendor to confirm. | Noted. But please be note that for top and bottom cap (flat type) will be considered Roark Handbook. | Noted and closed |  |
| 27. | Type of Flanges | Using Slip-on type flanges are not permitted for pressure vessels. For pressurized vessel just weld neck flange is acceptable. | Because tank is atmospheric therefore we considered slip on. | Noted and closed |  |
| 28. | Ladder and platforms | Ladder and platforms shall be designed by vendor in accordance with “Standard drawing for pressure vessel [BK-GNRAL-PEDCO-000-ME-DW-0001]. Besides, sufficient internal access by using Internal ladder and/or ladder rungs shall be considered by Vendor. | This document is not existed. Please send us for review. | Standard drawing for pressure vessel and heat exchanger has been issued as a MR attachment |  |
| 29. | Gaskets | Gaskets shall be considered as per project specifications. Vendor to confirm. | Noted. | Closed. |  |
| 30. | Calculation for Platforms | Calculation is required for those platforms either of following specified cases: - Platforms which their geometry (plan) does not covered by L&P standard drawings, - Platforms which having piping loads more than 400kg vertically or 200 kg horizontally. - Whole platform structures for above-mentioned platforms shall be submitted for review/approval. | There is no platform for this package because top cover is flat. | Noted and closed |  |
| 31. | Using leg supports | Limitations on weight/size of vertical vessels for using leg supports as per project specification shall be considered by Vendor. In any other cases (except for small vessels mounted on skid) skirt support shall be considered for vertical vessels by Vendor. However, any deviations from project specification shall be approved by purchaser. | We didn’t any limitation for this item our tank is Atmospheric and top/bottom flat cap and will be considered Lug/anchor chair for this. | Noted and closed |  |
| 32. | Hydrostatic test | Under the condition of the hydrostatic test, the stress shall not exceed 90 percent of the minimum specified yield strength of the material at testing temperature. For vertical vessels, which are shop-tested in the horizontal position, the shop test pressure must be increased by the hydrostatic head corresponding to the vessel field- tested full of water in the vertical position, in compliance with the calculation note. Vendor to confirm. | Noted. | Noted and closed |  |
| 33. | MAWP | For pressure vessels, Nozzle necks, nozzle reinforcement and flanges shall not be limiting elements in the determination of maximum allowable working pressure. If nozzle necks, nozzle reinforcement or flanges prove to be limiting elements, the MAWP shall be limited to the design pressure. | Our tank is atmospheric. | Noted and closed |  |
| 34. | Chemical Cleaning | Chemical Cleaning, Pickling & Passivation for Stainless Steel Parts are in Vendor’s scope. | Noted. | Closed |  |
| 35. | Surface preparation | Surface preparation and painting shall be in accordance with Specification for Painting Doc. No. BK-GNRAL-PEDCO-000-PI-SP-0006. Vendor to confirm. | Noted. | Closed |  |
| 36. | Inhibition materials | Inhibition materials against internal corrosion for transportation and long-time storage at stockyard is in vendor scope of supply. Requirements of section 8.2 of Project Specification for Pressure Vessels (BK-GNRAL-PEDCO-000-ME-SP-0001) for all vessels shall be followed by vendor. Bidder to Confirm. | Tank is S.S.316L and there is no needed inhibitor material. | Closed |  |
| 37. | Removable cover | The Tanks which will be filled by solid chemical diluted in place shall have fixed roof with segmental removable cover. | Not applicable. | Manhole or handhole shall be considered for accessing on the tank . |  |
| 38. | Comments on Vendor’s Proposal and its attachments | Please refer to the Attachment #1 of this TCL for other Mechanical comments on the offer. |  |  |  |
| PIPING & MATERIAL |  |  |  |  |  |
|  | General Arrangement | Please send us General Arrangement Drawing of Chemical Injection Package. | Sample GAD will be issued. | Shall be Sent by the vendor in the next review |  |
|  | PMS | Project PMS shall be followed by vendor. | Based on flow rate (2.2 lit/h) and pressure we considered suitable tubing inside the package. This item is considered for all prominent manufacturer in the world and best performance for this applicable because tubing is suitable for 420 barg. | Project PMS shall be followed by vendor. |  |
|  | VPIS | VPIS will be finalized later. | Noted. | Noted |  |
| INSTRUMENT & CONTROL |  |  |  |  |  |
|  | Control System Requirements | VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0004 and provide the requirement of type A package as mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. Signal details and communications shall be followed as per project P&ID. | Noted. But because LCP is relay based we can not receive analogue from LT. this item must be sent to DCS and Low Trip sent to LCP from DCS. | Noted |  |
|  | Panel Requirements | VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP- 004 for panels mounted field panels and all other details mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | Noted. | Closed |  |
|  | Instrumentation | Regarding supplying instrument on datasheet, bidder is requested to consider all instruments mentioned on project datasheet and Project P&ID. VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0001 for instrumentation devices and all other details mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | Noted. | Closed |  |
|  | Instrumentation Valves | VENDOR shall follow below documents for valves (if any) and other documents as mentioned in these documents. - BK-GNRAL-PEDCO-000-IN-SP-0005 - BK-GNRAL-PEDCO-000-IN-SP-0006 - BK-GNRAL-PEDCO-000-IN-SP-0007 VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | Document SP-0005 is not exist. Please send us. | Noted. Will be sent attached to TCL |  |
|  | Connection with MCC | If MCC is supplied by VENDOR all interfaces shall be supplied by VENDOR. Below signals are typically defined in this project to be provided for electrical interfaces: - Start command (2 sec high pulse) - Stop command (2 sec high pulse) - Trip command (low signal for trip) - Run/Stop Status (high signal for run status) - Local/Remote status (high signal for local status) - Tripped on Fault (high signal for fault status) - Available for remote control (high signal for available status) Detail signal requirements as per P&ID shall be followed. | MCC is out of vendor scope. We have one local control panel. | Not accepted. Motor and mixer control is by vendor. only 400 VAC uncontrolled power will be delivered to vendor. |  |
|  | Cable | VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0010 for cables and all other details mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | Noted. | Closed |  |
|  | Terminals | All terminals shall be screw type. VENDOR shall note that each core/pair/etc. of cable shall be wired to dedicated terminal | Noted. | Closed |  |
|  | Local Panel Dimension | VENDOR shall specify the estimated dimension of panels. | We suggest 800X1000X230 mm. but if LCP is ATEX, dimension will be revised. Please clarify this item. | Noted |  |
|  | Required Power | VENDOR shall specify the estimated power required (non-UPS and UPS) | All power inside the package is non-UPS. And required power is max. 6 kW. | Package shall be installed in safe area. IP 65 is requested at least. |  |
|  | Special Tools | VENDOR shall supply all special tools for compressor and axillary devices. This is included the special cables (not mentioned in BK-GNRAL-PEDCO-000-IN-SP-0010), MODBUS sockets, software and etc. The list shall be provided separately. | There is no needed special tools. | Noted |  |
|  | Protection Instruments | The protective instruments shall be according to API-670 and NFPA 20. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | Please specified Location Zone. | Package shall be installed in safe area |  |
|  | Start-up | VENDOR shall clearly state the start-up sequence. It shall be mentioned if any additional instrument or valve is required. Also, the interface signals shall be mentioned (if any) | We considered PID and there is not needed any additional instrument. | Noted |  |
|  | Spare part | VENDOR shall supply all commissioning/ 2 years spare part as per NISOC procedure, attached to PMR | Noted. | Closed |  |
| SAFETY |  |  |  |  |  |
|  | Sound Level | Noise level of Machinery / valves inside the package should not exceed 85 dbA @1m. | Noted. | Closed |  |
| ELECTRICAL |  |  |  |  |  |
|  | Specification | All electrical equipment shall comply with electrical references & standard that mentioned on material requisition. IPS-E-EL-100 (1), IPS-M-EL-131 (2) & IPS-M-PM-290(2). | Noted. | Closed |  |
|  | Vendor Scope of Work | All documents related to electrical equipment shall be submitted by vendor such as preliminary load list, electrical equipment list, motor data sheet, motor outline drawing & etc. | Load list will be issued after PO. But we required 6 kW power for this package. | Closed |  |
|  | Vendor Scope of Work | Vendor list & sub vendor list of manufacture shall be according to project AVL. | Noted. | closed |  |
|  | Vendor Scope of Work | The cable from switchgear to package panel is by client, but the cable in the package form panel to each equipment is by vendor. In other word, from client point of view, there is only one load which assumed the power demand of package is the total load. (Tie in between client & vendor is main panel). | Noted. Please be note that we needed 3 phase+Null+PE. | Closed, 400v/50hz/3ph will be supplied by contractor. |  |
|  | Vendor Scope of Work | According to item 4, the total electrical demand is required. | 6 kW is enough. | closed |  |
|  | Vendor Scope of Work | Since the power & control cables in the skid is by vendor, therefore the cable list in the package shall be according to “BK-GNRAL-PEDCO-000-EL-SP-0014”. Interconnection in the skid is by vendor. | Noted. | closed |  |
|  | Vendor Scope of Work | Supplier shall design the routing of the power & control cable inside package. | Noted. | closed |  |
|  | Vendor Scope of Work | If AC UPS or DC UPS & batteries are required, vendor shall provide all necessary documents (such as calculation, list etc.) & supply required equipment according to purchaser standards. | There is no need. | closed |  |
|  | Spare Part | A complete set of spare parts for commissioning shall be supplied for each motor. | Noted. | closed |  |
|  | Test & Inspection | The equipment shall be factory tested. Certified copies of test reports shall be submitted to the purchaser. | Noted. | closed |  |
|  | Vendor Scope of Work | Data sheet & Specification of LV induction motor have been attached. Please follow them. | Noted. | closed |  |
|  | Vendor Scope of Work | Deviation & clarification form shall be issued by vendor | Noted. | closed |  |
|  | Vendor Scope of Work | Deviation list for anti-condensation of motor shall be according to IPS-M-EL-131(2). | Because all motors is below 3 kW therefore anticondensation is not applicable. | closed |  |
| STRUCTURE |  |  |  |  |  |
|  | Earthquake load | Based on STD2800 this site is located at High Risk Area which is named Seismic Zone 2. also according to ASCE 7 (2010) Seismic Zone is equal to Zone 3 with Seismic Importance Factor 1.25 | Noted. | Closed |  |
|  | Wind | According to project spec. mean hourly with 50Yr return period speed shall be considered 120 Km/hr. | Noted. | Closed |  |
|  | Anchor bolt | The size and type and location of the anchor bolts should be provided in a guide map. | Noted. | Closed |  |
|  | Skid | The exact dimensions & size of the skid and the proper alignment under the skid should be determined. | Noted. After Po. | Closed |  |
|  | Loads and center mass | The static & dynamic loads of the equipment and the center of gravity of it shall be determined. | Only static is reported because 9/10 of weight of package is for fixed equipment. | Not applicable, The static & dynamic loads of the equipment and the center of gravity of it shall be determined. |  |
|  | Room layout | If this equipment must be kept in the room, all the necessary information of the room layout, such as the drain system and the required network, or where the air ducts pass, and any required requirements must be clearly mentioned and presented in a layout. | Noted. | Closed |  |
|  | References | The following codes & standards should be considered in the civil & structure section: AWS , ASCE7-10 , INBC6 | Noted. | Closed |  |