## COVER
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE FOR ESD SYSTEM
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | TB | 0002 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
TBE FOR ESD SYSTEM نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | JUL.2023 |  | IFI |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Sadeghian
D01 |  | OCT.2023 |  | IFI |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D00 |  | JUN.2023 |  | IFI |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: | CLIENT Approval
Class: 3 |  |  |  | CLIENT Doc. Number: F0Z-709270
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## TBE for ESD system
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE FOR ESD SYSTEM
شماره پیمان: |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات | رشته |  | نوع مدرک | سریال |  | نسخه
9184 – 073 - 053 |  |  | BK |  | GCS |  | PEDCO |  | 120 | IN |  | TB | 0002 |  | D02
REQ. NAME : |  | PMR For ESD System |  |  | BIDDER NAME: |  |  | IDEH GLOBAL Co. |  |  | CONTROL SAZAN POOYANDEH |  |  | PARS CONTROL PISHRO (HAVAYAR)
REQ. NO. : |  | BK-GCS-PEDCO-120-IN-MR-0002 |  |  | QUOTATION NO.: |  |  | 855S-EOB-MA Rev.1 |  |  | Q-CSP-1400-0178 Rev.E |  |  | 024/TC/06/09 Rev.05
REQ. REV. : |  | D02 |  |  | QUOTATION DATE: |  |  | 2024-06-12 |  |  | 2024-07-14 |  |  | 2024-07-10
CONTROLLER BRAND: | [7 empty] | DCS: HONEYWELL ESD: EMERSON |  |  | DCS: SIEMENS ESD: HIMA |  |  | DCS: SIEMENS ESD: EMERSON
NO. | DESCRIPTION |  | REFERENCE / SPECIFIED / REQUIREMENTS |  |  |  |  | MEETS REQUISITION REQUIREMENTS
[8 empty] | "A" |  |  | "B" |  |  | "C"
A | Scope of Work And Supply
A1 | Scope of Work
A1-1 | Scope of Work And Supply |  | ESD SYSTEM |  |  |  |  | Confirmed,Emerson |  |  | confirmed |  |  | Emergency Shutdown System
A1-2 | Reference documents for proposal (MR, spec, datasheet & etc.) |  | According to the last revision |  |  |  |  | Confirmed |  |  | confirmed |  |  | CONFIRMED
A1-3 | Delivery Date |  | B.V. |  |  |  |  | 180 Days |  |  | 4 months after AP received |  |  | 6 mounths
A1-4 | Delivery Place |  | Ex. Work |  |  |  |  | Karaj/Payam Airport |  |  | confirmed |  |  | EXW Pars Control Pishro factory
A1-5 | Bid Validity Period |  | B.V. |  |  |  |  | 180 Days |  |  | 3 months |  |  | 2 weeks
A1-6 | GUARANTEE |  | The guarantee period shall be eighteen (18) months from the date of delivery or twelve (12) months from the installation date of each equipment/packages at site |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
A1-7 | MANUFACTURER (VENDOR LIST) |  | AVL |  |  |  |  | Confirmed |  |  | confirmed, HIMA FOR F&G (HIQUAD) |  |  | AVL-MOP-NPC
A1-8 | SPARE PARTS |  | 2 YEARS / START-UP AND COMMISSIONING according to document no.: E&D-QC-SP-1 |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
A1-9
A2 | limit of supply
A2-1 | System Cabinet |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | 3 CABINET
A2-2 | Marshalling cabinet, including field terminals |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
A2-3 | Matrix Panel |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | no
A2-5 | ESD Printer |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
A2-6 | ESD Engineering Workstation |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
A2-7 | Erection, Pre-Commissioning and commissioning |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
A2-8 | ESD System |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
A2-10 | AC/DC Segregation |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
A2-11 | IS & NIS Segregation |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
A2-12 | Pre- Fabricated cable between I/O card & marshaling |  | As requested (Depends on the Brand of ESD System) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
A2-13 | Interface with other system |  | As requested per spec and block diagram |  |  |  |  | Confirmed |  |  | confirmed |  |  | With DCS System Accepted
B | Automation Stations - Hardware Details
B1 | Power Supply Unit
B1-1 | Nominal Input Voltage |  | 110VAC 50 HZ UPS by two separate (dual redundant) feeder from UPS |  |  |  |  | Confirmed |  |  | confirmed |  |  | Noted
B1-2 | Unaffected frequency and voltage variations |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B1-3 | Short Circuit Protection |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B1-4 | Reporting Status : | [9 empty] | confirmed
| Delivery Contact |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | not accepted
| Delivery Software Alarm |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B1-5 | Redundancy |  | As requested (according to the I/O List) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B1-6 | Power outage without any ESD trip |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B1-7 | Internal voltage adaptor for 24VDC |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B1-8 | 110VAC UPS Power consumption |  | W (Shall be specified by vendor) |  |  |  |  | 2.5 KW |  |  | Plesae see offer attachment(#12) |  |  | 2kw
B1-9 | Allowed load (max) |  | 60% of capacity |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B1-10 | Qty. |  | Shall be specified by vendor |  |  |  |  | 2 |  |  | 4 |  |  | 2
B2 | Central Processing Unit (CPU)
B2-1 | Watch-dog system |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B2-2 | Response time from input change to output action |  | msec |  |  |  |  | 100ms |  |  | <100 ms |  |  | Refer to the catalog
B2-3 | Redundancy |  | As requested (according to the I/O List) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B2-4 | PLC Scan time |  | msec |  |  |  |  | 50 ms |  |  | Below 100ms; |  |  | Refer to the catalog
B2-5 | Power outage without PLC trip |  | msec |  |  |  |  | 100ms |  |  | 20msec |  |  | Refer to the catalog
B2-6 | Type |  | Shall be specified by Vendor |  |  |  |  | SQ 3008 |  |  | H51Q-HRS HIMA (HIQUAD) |  |  | Controller MD Plus - 48MB user memory
B2-7 | Make |  | Shall be specified by Vendor |  |  |  |  | Europe |  |  | HIMA, Germany |  |  | EMERSON
B2-8 | CPU loading factor |  | Less than 70 % of processing capacity and memory |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B3 | Memories
B3-1 | Type for data table |  | Shall be specified by Vendor |  |  |  |  | Excel Format |  |  | Boolean, real, message, timer, constant |  |  | 48MB user memory
B3-2 | Type for program |  | Shall be specified by Vendor |  |  |  |  | DeltaV Format |  |  | CFC, Ladder,… |  |  | 48MB user memory
B3-3 | Non-Volatile Buffer Memory |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B3-4 | Non-Volatile Application Program |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B3-5 | Battery Back Up |  | six (6) months |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B3-6 | Write protection system |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B3-7 | Data types existing in each controller different from I/O types (Integer, Boolean, Real, Message, Timer, Constant) |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B4 | Digital I/O Cards
B4-1 | Interference immunity (RFI / EMI) |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B4-2 | Capability of removing and inserting under power |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | It is possible for the redundant system
B4-3 | Individually Opto-isolated |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B4-4 | Compatible slots for inputs and outputs (hot swap) |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B4-5 | Status LEDs (per card, per channel, etc.) |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B4-6 | Capability of filtering and timing |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B4-7 | Output rating |  | As requested |  |  |  |  | Confirmed |  |  | 24 V DC |  |  | Confimed
B4-8 | Input voltage |  | As requested |  |  |  |  | Confirmed |  |  | 24 V DC |  |  | Confimed
B4-9 | Number of channel per card (DI/DO) |  | Shall be specified by Vendor |  |  |  |  | 16 |  |  | 16 Ch for DI, 8 Ch for DO |  |  | 16 Chanel
B4-10 | MANUFACTURER, TYPE & QTY OF DI MODULE |  | Shall be specified by Vendor |  |  |  |  | Emerson/VS3202 , 10 |  |  | HIMA, F3236, 6 |  |  | Delta V SLS 1508 Redundant Logic Solver QTY: 15
B4-11 | MANUFACTURER,TYPE & QTY OF DO MODULE |  | Shall be specified by Vendor | [7 empty] | HIMA, F3330, 28 |  |  | Delta V SLS 1508 Redundant Logic Solver QTY: 15
B4-12 | l/O self-diagnostic system |  | The I/O cards shall have fault diagnostics and status indications |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B4-13 | Capability Of replacement under power |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B4-14 | Redundancy |  | As requested (according to the I/O List) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B5 | Digital Inputs
B5-1 | Powered |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | sitop power considerated
B5-2 | Overload Voltage/ surge current |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B5-3 | Number of channels per card |  | Shall be specified by vendor |  |  |  |  | 16 |  |  | 16 Ch for DI |  |  | 16 Chanel
B5-4 | Qty. of redundant DI (channel) |  | As requested (according to the I/O List) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B6 | Digital outputs
B6-1 | Interposing Relays |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B6-2 | Voltage rating |  | 24 VDC , at least 300 mA |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B6-3 | Capability to be forced |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B6-4 | Termination board common polarity |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B6-5 | Number of channels per card |  | Shall be specified by vendor (Not more than 32 channels) |  |  |  |  | 16 |  |  | 8 Ch for DO |  |  | 16 Chanel
B6-6 | Switching time :
| Delivery From off to on state |  | Shall be specified by vendor |  |  |  |  | 2 mA |  |  | <50 µs |  |  | Refer to the catalog
| Delivery From on to off state |  | Shall be specified by vendor |  |  |  |  | 0.25 mA |  |  | <50 µs |  |  | Refer to the catalog
B6-7 | Fuse relay contact |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B7 | Analogue I/O Cards
B7-1 | Individual Channel Fusing |  | Shall be specified by vendor |  |  |  |  | 2A |  |  | confirmed |  |  | Confimed
B7-2 | Availability of a Simulation Device |  | Shall be specified by vendor |  |  |  |  | 50ms |  |  | confirmed |  |  | Confimed
B7-3 | Galvanic-isolated |  | Shall be specified by vendor |  |  |  |  | Each channel is optically isolated from the system and factory |  |  | confirmed, between the channels and channels |  |  | Confimed
B7-4 | Scan Time Cycle |  | msec |  |  |  |  | 100ms |  |  | <20 ms@50 Hz |  |  | Confimed
B7-5 | Conversion time |  | msec |  |  |  |  | 50ms |  |  | <60ms@50Hz |  |  | Confimed
B7-6 | Interference Immunity (RFI / EMI) |  | Needed / IEC 61000 |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B7-7 | Capability of Replacement Under Power (hot swap) |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B7-8 | Individual analogue / digital and digital / analogue converters |  | Yes -per module |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B7-9 | Individual signal isolation, galvanic isolation |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B7-10 | Software calibration |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | It is not applicable
B7-11 | Diagnostic and status LEDs (per card, per channel, etc.) |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B7-12 | Quantity of channels per card (AI / AO) |  | Shall be specified by Vendor (Not more than 16) |  |  |  |  | 16 |  |  | 8 channels |  |  | 16 Chanel
B7-13 | Type of signal :
| Delivery Input card |  | 4-20mA |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Delivery Output card |  | 4-20mA |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B7-14 | Accuracy |  | Shall be specified by vendor |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B7-15 | Accuracy |  | equal or better than 0.2% of Full Scale |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B7-16 | Linearity |  | better than +/- 0.025% |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B7-17 | A/D Resolution |  | A/D conversion will be preferred point to point (minimum of 16 bits) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B7-18 | Diagnostic and Status LEDs |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B7-19 | Termination Board Common Polarity |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B7-20 | Number Of Channels Per Card |  | Shall be specified by vendor |  |  |  |  | Confirmed |  |  | confirmed |  |  | 16 CH
B7-21 | Loop Power Supply :
| Delivery Internal |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
| Delivery External |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B7-22 | Self-test capability |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
B7-23 | Signal |  | 4-20 mA (24 V DC) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B7-24 | Redundancy |  | As requested (according to the I/O List) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B7-25 | MANUFACTURER, TYPE & QTY OF AI MODULE |  | Shall be specified by Vendor |  |  |  |  | Emerson/VS3202 , 5 |  |  | HIMA, F 6217, 18 |  |  | VS3202
B7-26 | MANUFACTURER, TYPE & QTY OF AO MODULE |  | Shall be specified by Vendor | [7 empty] | NA |  |  | VS3202
B7-27 | Monitoring for open or short circuit detection in standard |  | as per project specification |  |  |  |  | Confirmed |  |  | confirmed |  |  | as per project specification
B7-28 | HART protocol |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B7-29 | Barrier |  | As requested (according to the I/O List) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
B8 | Communications by serial link
B8-1 | Number of ports available per card |  | Shall be specified by Vendor |  |  |  |  | 2 |  |  | 1 Port per Card |  |  | 3 Port
B8-2 | Is there a specific arrangement in the controller or rack? |  | Shall be specified by Vendor |  |  |  |  | The controller rack is placed above the card racks |  |  | In Rack |  |  | YES
B8-3 | Communication/interface module Type |  | According to project and cyber security requirements |  |  |  |  | Confirmed |  |  | F 8621A |  |  | Modbus، Profibus، Ethernet/IP
B8-4 | Bit rate |  | Shall be specified by Vendor |  |  |  |  | Configurable with the DeltaV |  |  | 115.2 kb/s |  |  | 2x 10/100 Mbit/s
B8-5 | Protocol |  | As Bellow |  |  |  |  | Modbus RTU or ASCII protocol. |  |  | Modbus RTU |  |  | Modbus، Profibus، Ethernet/IP
B8-6 | Scan time |  | msec |  |  |  |  | 100 msec |  |  | <100 ms |  |  | Refer to the catalog
B8-7 | Serial Link Quantities with other systems |  | As Bellow |  |  |  |  | 2 |  |  | confirmed |  |  | It depends on the upstream system
B8-8 | Communications with other systems |  | According to the block diagram |  |  |  |  | Confirmed |  |  | confirmed |  |  | YES
B8-9 | MODBUS RTU MODULE TYPE/ QTY |  | Shall be specified by Vendor |  |  |  |  | SE4036P2/ 2 |  |  | F 8621A, 2 Cards |  |  | NO
B8-10 | MODBUS TCP/IP MODULE TYPE/ QTY |  | Shall be specified by Vendor |  |  |  |  | N/A |  |  | NA |  |  | YES
B8-11 | MODBUS RTU SOFTWARE LICENCE ORDER NO./ QTY |  | Shall be specified by Vendor |  |  |  |  | considered in the general license |  |  | MODBUS COPROCESSOR MODULE, H41Q,H51Q WITH ELOP II |  |  | NO
B8-12 | MODBUS TCP/IP SOFTWARE LICENCE ORDER NO./ QTY |  | Shall be specified by Vendor |  |  |  |  | considered in the general license |  |  | NA |  |  | YES / 1
B8-13 | Redundancy data highway |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | YES
C | Automation Stations - Technical Properties
C1 | Reliability
C1-1 | MTBF |  | Shall be specified by Vendor |  |  |  |  | Min 10000 hours |  |  | Plesae see offer attachment(#10), MTBFTOTAL= 156 Years |  |  | Refer to the catalog
C1-2 | MTTR |  | 4 Hours |  |  |  |  | Confirmed |  |  | availability better than 99.99% with MTTR of 8 hours for H system |  |  | Refer to the catalog
C1-3 | System Availability |  | Shall be specified by Vendor |  |  |  |  | 99.99% |  |  | Refer to offer attachment: 10-MTTR and MTBF Calculation |  |  | Refer to the catalog
C2 | Spare/ Space percent
C2-1 | Spare fully wired and installed |  | 0.2 |  |  |  |  | Confirmed |  |  | 0.2 |  |  | Confimed
C2-2 | Spare space |  | 0.2 |  |  |  |  | Confirmed |  |  | 0.2 |  |  | Confimed
C3 | Redundancy
C3-1 | CPU cards redundant |  | Yes (as per requested documents) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C3-2 | Communication interfaces |  | Yes (as per requested documents) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C3-3 | Main Power Supply Units redundant |  | Yes (as per requested documents) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C3-4 | I/Os redundant for digital I/Os |  | as per I/O List & Related specs (on Channel) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C3-5 | I/Os redundant for Analog I/Os |  | as per I/O List & Related specs (on Channel) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C3-6 | Power conditioner |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C4 | Diagnostics
C4-1 | On-line routine |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
C4-2 | Off-line routine |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
C4-3 | Standard displays |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
C4-4 | Standard alarms |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Refer to the catalog
C5 | System/Marshalling Cabinets
C5-1 | Type of cabinet/ frame |  | Standard size RITTAL type |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C5-2 | Width |  | 800mm |  |  |  |  | Confirmed |  |  | 800mm |  |  | Confimed
C5-3 | Depth |  | 800 mm |  |  |  |  | Confirmed |  |  | 600mm |  |  | Confimed
C5-4 | Height |  | 2000mm |  |  |  |  | Confirmed |  |  | 2000mm |  |  | Confimed
C5-5 | Cabinet metal work: minimum plate thickness |  | 2mm |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C5-6 | Plinth Base Frame |  | 100mm |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C5-7 | Racking System |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C5-8 | Internal Light |  | 230 VAC 1phase (controlled by door switches) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C5-9 | Convenient Outlet |  | 230 VAC 1phase |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C5-10 | 230VAC NON-UPS Power consumption (Per Station) |  | 230 VAC 1phase non-UPS |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C5-11 | Degree of Protection |  | IP 54 |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C5-12 | Access |  | Door access at the front and back |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C5-13 | Cooling Fan with fault alarm of HH temp. |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C5-14 | Dust filters |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C5-15 | Earthing / Grounding |  | Compliant to project earthing spec. |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C5-16 | Common Key Locks |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C5-17 | Door limit switch for lighting |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C5-18 | Cable entry |  | Bottom |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C5-19 | Paint color |  | Gray, RAL 7032/7035 |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C5-20 | ESTIMATED CELLS QTY |  | Shall be specified by Vendor |  |  |  |  | 2 |  |  | 3 |  |  | 3 PANEL
C5-21 | MANUFACTURER NAME / LOCATION |  | Shall be specified by Vendor |  |  |  |  | IRAN TABLO/ SAFA DASHT |  |  | Pars Tablo or Phase kar |  |  | TAVAN SANAT
C6 | Main Power Supply Unit
C6-1 | Work stations (Operator / Engineer) |  | 110 VAC (UPS) |  |  |  |  | Confirmed |  |  | confirmed |  |  | NUPS 230V AC
C6-2 | Printers |  | 110 VAC (UPS) |  |  |  |  | Confirmed |  |  | confirmed |  |  | 230V AC
C6-3 | System |  | 110 VAC (UPS) |  |  |  |  | Confirmed |  |  | confirmed |  |  | 230V AC
C6-4 | 110VAC UPS Power consumption (Per Station) |  | Watt |  |  |  |  | 450W |  |  | Refer to offer attachment: #12 Power consumption |  |  | 2KW
C6-5 | Power consumption per unit |  | Watt |  |  |  |  | 2.5 KW |  |  | 500 |  |  | 2KW
C6-6 | Allowed load per unit (max) |  | % of capacity |  |  |  |  | Confirmed |  |  | 30% |  |  | Compliant to project spec.
C6-7 | Redundancy |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
C6-8 | Qty. |  | Shall be specified by Vendor |  |  |  |  | 1 |  |  | 4 |  |  | Compliant to project spec.
D | WORKSATIONS
D1 | Operator work station
D1-1 | Operating system |  | The latest revision of original windows |  |  |  |  | Win 10 |  |  | confirmed |  |  | Confimed
D1-2 | CPU |  | Core i5 |  |  |  |  | Confirmed |  |  | Core i5 2400 |  |  | Confimed
D1-3 | RAM |  | 8 GB (As minimum) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D1-4 | HD |  | 1 TB |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D1-5 | DVD Writer |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D1-6 | Color monitor (Industrial LED monitor: heavy duty) |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D1-7 | Size |  | 32" (As minimum) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D1-8 | Keyboard type |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D1-9 | MODEL/MANUFACTURER (SYSTEM + MONITOR) |  | Shall be specified by Vendor |  |  |  |  | HP Z440 / Dell S3219D |  |  | LS32BG650EM ,Samsung |  |  | LG / G+
D1-10 | QTY (SYSTEM + MONITOR + KEYBOARD) |  | As requested |  |  |  |  | Confirmed |  |  | 2, 4, 2 |  |  | 1 st
D1-11 | Mimic displays |  | As requested |  |  |  |  | Confirmed |  |  | No, For ESD confirmed |  |  | NO
D2 | Engineering & Maintenance workstation
D2-1 | Operating system |  | The latest revision of original windows |  |  |  |  | Win 10 |  |  | confirmed |  |  | Confimed
D2-2 | CPU |  | Core i5 |  |  |  |  | Confirmed |  |  | Core i5 2400 |  |  | Confimed
D2-3 | RAM |  | 8 GB (As minimum) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D2-4 | HD |  | 1 TB |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D2-5 | DVD Writer |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | not accepted
D2-6 | Color monitor (Industrial LED monitor: heavy duty) |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Compliant to project spec.
D2-7 | Size |  | 32" (As minimum) |  |  |  |  | Confirmed |  |  | confirmed |  |  | 32"
D2-8 | Keyboard type |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | A4TECH
D2-9 | MODEL/ MANUFACTURER (SYSTEM + MONITOR) |  | Shall be specified by Vendor |  |  |  |  | HP Z440 / Dell S3219D |  |  | LS32BG650EM ,Samsung |  |  | LG / G+
D2-10 | QTY (SYSTEM + MONITOR + KEYBOARD) |  | As requested |  |  |  |  | Confirmed |  |  | 2, 2, 2 |  |  | 1 st
D3 | Operator interface
D3-1 | Data display : | [12 empty] | Confimed
D3-2 | Number available |  | Shall be specified by Vendor |  |  |  |  | Unlimited |  |  | >100 pages, as per Custumer requests |  |  | TBD
D3-3 | Access procedure |  | Shall be specified by Vendor |  |  |  |  | Confirmed |  |  | Yes |  |  | TBD
D3-4 | Overview |  | Shall be specified by Vendor |  |  |  |  | Confirmed |  |  | Yes |  |  | Confimed
D3-5 | Unit display |  | Shall be specified by Vendor |  |  |  |  | Confirmed |  |  | Yes |  |  | Confimed
D3-6 | Process display as per station |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-7 | Group overview display |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-8 | Detail display |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-9 | Parameter display |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-10 | Trend overview display |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-11 | Maintenance display |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-12 | Report/ journal overview |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-13 | Alarm and event list and logging : | [12 empty] | Confimed
| Number of priority level assignable |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Alarm and event time discrimination |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Displayed data for each alarm and event of the list |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| File size assignable |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-14 | Active process alarm list | Active process alarm list | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-15 | Active hardware alarm list | Active hardware alarm list | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-16 | Cleared hardware alarm List | Cleared hardware alarm aist | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-17 | Active system alarm list | Active system alarm list | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-18 | Cleared system alarm list | Cleared system alarm list | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-19 | Event list | Event list | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-20 | Operator change logging | Operator change logging | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-21 | Trend logging | Trend logging | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-22 | Trend display : | Trend display : | [11 empty] | Confimed
| Number of tracked variables | Number of tracked variables | Shall be specified by Vendor |  |  |  |  | Depend on HDD Size |  |  | >50 variables as per Custumer requests |  |  | TBD
| Number of variables per display | Number of variables per display | Shall be specified by Vendor |  |  |  |  | 1200 |  |  | >200 variables as per Custumer requests |  |  | TBD
| Variable types allowed (Analogue / digital) | Variable types allowed (Analogue / digital) | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Display data on a trend display (PV/MV/SP) | Display data on a trend display (PV/MV/SP) | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Zoom capability | Zoom capability | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Access procedure (Call-up) | Access procedure (Call-up) | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| HD space of 30 days of time storage (every 1 sec) | HD space of 30 days of time storage (every 1 sec) | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-23 | Process graphic display : | Process graphic display : | [11 empty] | Confimed
| Object orientation | Object orientation | Shall be specified by Vendor |  |  |  |  | Confirmed |  |  | Yes |  |  | TBD
| Data type available | Data type available | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Number available | Number available | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Number of data available per each process graphic display | Number of data available per each process graphic display | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Number of standard symbols available in library | Number of standard symbols available in library | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Number of user's symbols configurable | Number of user's symbols configurable | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Number of elementary symbols configurable (on a pixel basis) | Number of elementary symbols configurable (on a pixel basis) | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Availability of hidden messages symbols | Availability of hidden messages symbols | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-24 | Capacity of windowing : | Capacity of windowing : | [11 empty] | Confimed
| - Access procedure (Call-up) | - Access procedure (Call-up) | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| - Panning scrolling modes for moving throughout graphic pages | - Panning scrolling modes for moving throughout graphic pages | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-25 | Reports : | Reports : | [11 empty] | Confimed
| DeliveryStandard reports | Standard reports | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| DeliveryUser's format reports | User's format reports | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Number of each available : | Number of each available : | [11 empty] | Confimed
| DeliveryStandard | Standard | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| DeliveryUser's format | User's format | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Set up mode : | Set up mode : | [11 empty] | Confimed
| DeliveryConfiguration | Configuration | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| DeliveryProgramming | Programming | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Access procedure | Access procedure | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Print out configuration | Print out configuration | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-26 | System configuration display : | System configuration display : | [11 empty] | Confimed
| Inputs/ outputs | Inputs/ outputs | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Logic loop | Logic loop | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Trend files | Trend files | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Process unit | Process unit | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-27 | Group display : | Group display : | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Alarm and event list | Alarm and event list | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| Standard message | Standard message | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
| User massage | User massage | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-28 | Maintenance and trouble-shouting purpose display : | Maintenance and trouble-shouting purpose display : | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-29 | System and data Buses | System and data Buses | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-30 | Diagnostic test display | Diagnostic test display | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-31 | Trouble shooting display | Trouble shooting display | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D3-32 | Performance : | Performance : | [11 empty] | Confimed
| Display call up time | Display call up time | < 2 sec. | < 2 sec. |  | < 2 sec. |  | Confirmed |  |  | confirmed |  |  | TBD
| Display refresh time | Display refresh time | 1 Sec | 1 Sec |  | 1 Sec |  | Confirmed |  |  | confirmed |  |  | TBD
| Time tagging resolution | Time tagging resolution | 0.005 Sec. | 0.005 Sec. |  | 0.005 Sec. |  | Confirmed |  |  | confirmed |  |  | TBD
| other performances | other performances | as per project specification | according to MMI Spec. 3GSP-00-BE-IN-SP-0008 |  | according to MMI Spec. 3GSP-00-BE-IN-SP-0008 |  | Confirmed |  |  | confirmed |  |  | Confimed
D4 | Printer
D4-1 | Type / Make |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | TBD
D4-2 | Size |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | TBD
D4-3 | MODEL / MANUFACTURER |  | Shall be specified by Vendor |  |  |  |  | P1108 , HP |  |  | Color Laser hp 150a and hp M12w |  |  | HP/canon
D4-4 | Qty. |  | As requested |  |  |  |  | 1 |  |  | 2 |  |  | 1
D5 | ESD Hardwire Console Panel
D5-1 | Supplier |  | Shall be specified by vendor |  |  |  |  | Local |  |  | Pars Tablo or Phase kar |  |  | Compliant to project spec.
D5-2 | Material / thickness |  | Shall be specified by vendor |  |  |  |  | as per project Spec |  |  | 2 mm |  |  | Compliant to project spec.
D5-3 | Dimensions |  | Shall be specified by vendor |  |  |  |  | as per project Spec |  |  | 1200mm x 600mm x 1000mm |  |  | Compliant to project spec.
D5-4 | Degree of Protection |  | min. IP 54 |  |  |  |  | Confirmed |  |  | confirmed |  |  | Compliant to project spec.
D5-5 | Override Key Switches |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Compliant to project spec.
D5-6 | Push Buttons & Lamps |  | Yes |  |  |  |  | Confirmed |  |  | confirmed |  |  | Compliant to project spec.
D5-7 | Access |  | Rear |  |  |  |  | Confirmed |  |  | confirmed |  |  | Compliant to project spec.
D5-8 | Qty. of Lamps |  | As Per I/O List |  |  |  |  | Confirmed |  |  | confirmed |  |  | Compliant to project spec.
D5-9 | Qty. of Push Buttons & Key Switches |  | As Per I/O List |  |  |  |  | Confirmed |  |  | confirmed |  |  | Compliant to project spec.
D5-10 | Qty. of Console Panel |  | 1 cubicle |  |  |  |  | Confirmed |  |  | confirmed |  |  | Compliant to project spec.
D6 | Control Room Furniture
D6-1 | Desks |  | As requested, according to CR building layout Desk (Desks have been made of white MDF with black PVC tape in environment of MDF) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D6-2 | Operator armchairs |  | As requested, according to CR building layout |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
D7 | SOFTWARES & LICENCES
D7-1 | Kind of configuration system backup : | Kind of configuration system backup :
| For controller | For controller | Shall be specified by Vendor |  |  |  |  | VE31RED |  |  | Full redaundant |  |  | Confimed
| For operator workstation | For operator workstation | Shall be specified by Vendor |  |  |  |  | VE2104 |  |  | ELOP II PROFESSIONAL FOR HIMA PES PROGRAMMING, ENGLISH, FULL PACKAGE, HARD LOCK FOR USB INTERFACE |  |  | Confimed
| For engineer workstation | For engineer workstation | Shall be specified by Vendor |  |  |  |  | VE2102 |  |  | ELOP II PROFESSIONAL FOR HIMA PES PROGRAMMING, ENGLISH, FULL PACKAGE, HARD LOCK FOR USB INTERFACE |  |  | Confimed
D7-2 | Kind and quantity of Supplier's software for SCS functioning | Kind and quantity of Supplier's software for SCS functioning | Shall be specified by Vendor |  |  |  |  | N/A |  |  | ELOP II PROFESSIONAL FOR HIMA PES PROGRAMMING, ENGLISH, FULL PACKAGE, HARD LOCK FOR USB INTERFACE |  |  | Confimed
D7-3 | Trend | Trend | Shall be specified by Vendor |  |  |  |  | N/A |  |  | on 2 server workstation |  |  | Confimed
D7-4 | Free space | Free space | Shall be specified by Vendor |  |  |  |  | N/A |  |  | 30% |  |  | Confimed
D7-5 | Monitoring and control | Monitoring and control | Shall be specified by Vendor |  |  |  |  | Include operator station |  |  | Yes |  |  | Confimed
D7-6 | Original Licenses | Monitoring and control | Shall be specified by Vendor |  |  |  |  | Confirmed |  |  | 6 |  |  | Confimed
S | SERVICES
S1 | Service
S1-1 | F.A.T (days) |  | Shall be specified by Vendor |  |  |  |  | 16 Days |  |  | 5 (days) |  |  | Confimed
S1-2 | S.A.T (days) |  | Shall be specified by Vendor |  |  |  |  | 25 Days |  |  | 10 (days) |  |  | Confimed
S1-3 | Start Up & commissioning |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
S1-4 | Organizational structure |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
S1-5 | Pre-commissioning and commissioning |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
S1-6 | Packing |  | According to BK-GNRAL-PEDCO-000-QC-PR-0045: Packing, Marking, Transportation Procedure |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
S1-7 | Transportation |  | According to BK-GNRAL-PEDCO-000-QC-PR-0045: Packing, Marking, Transportation Procedure |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
S1-8 | On-call or maintenance availability |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
S1-9 | Engineering |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
S1-10 | Cyber Security |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
S1-11 | Synchronize between systems |  | Needed |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
S2 | Codes and Standards for ESD, F&G system
S2-1 | Compliant to ESD specification |  | IEC 61508 or TUV class or DNV 19250 |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
S2-2 | Compliant to F&G specification |  | IEC 61508 or TUV class or DNV 19250 |  |  |  |  | Confirmed |  |  | confirmed |  |  | NA
S3 | Documentation
S2-1 | Standard |  | According to Project Specification |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
S2-2 | Project (configuration drawings) |  | According to Project Control System Configuration |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
S2-3 | Self-documentation system |  | As requested. |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
S4 | Training
S3-1 | Operator |  | Needed (According to SPECIFICATION FOR CONTROL SYSTEM) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Compliant to The project spec.
S3-2 | Programmer |  | Needed (According to SPECIFICATION FOR CONTROL SYSTEM) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Compliant to The project spec.
S3-3 | Maintenance |  | Needed (According to SPECIFICATION FOR CONTROL SYSTEM) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Compliant to The project spec.
S5 | Spare part
S4-1 | Start-up & commissioning |  | According to PROJECT SPARE PART SUPPLY PROCEDURE (Doc. No. E&D-QC-SP-1) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
S4-2 | 2 years |  | According to PROJECT SPARE PART SUPPLY PROCEDURE (Doc. No. E&D-QC-SP-1) |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
S6 | Specific tools required
S6-1 | Maintenance tools |  | Optional |  |  |  |  | Confirmed |  |  | confirmed |  |  | Compliant to project spec.
S6-2 | Operation tools |  | Optional |  |  |  |  | Confirmed |  |  | confirmed |  |  | Compliant to project spec.
S6-3 | Engineering tools |  | Optional |  |  |  |  | Confirmed |  |  | confirmed |  |  | Compliant to project spec.
U | Others
U-1 | System model / type |  | Based on Technical Offer , Shall be specified by Vendor |  |  |  |  | Emerson / DeltaV S Series |  |  | HIMA Hiquad H51q |  |  | TBD
U-2 | Country of origin for major components : |  | Based on Technical Offer , Shall be specified by Vendor |  |  |  |  | Europe |  |  | Germany |  |  | TBD
| Controller |  | Based on Technical Offer , Shall be specified by Vendor |  |  |  |  | SQ 3008 |  |  | H51Q-HRS MODULAR AUTOMATION SYSTEM |  |  | TBD
| Memory |  | Based on Technical Offer , Shall be specified by Vendor |  |  |  |  | 96 MB |  |  | H51Q-HRS MODULAR AUTOMATION SYSTEM |  |  | TBD
| I / O Cards/Isolators/ Barriers |  | Based on Technical Offer , Shall be specified by Vendor |  |  |  |  | As per Project Spec |  |  | Yes, Refer to Our offer, Rev E |  |  | TBD
| Communication Module |  | Based on Technical Offer , Shall be specified by Vendor |  |  |  |  | SE4036P2 |  |  | Yes, Refer to Our offer, Rev E |  |  | TBD
| Bus Controller |  | Based on Technical Offer , Shall be specified by Vendor |  |  |  |  | SE3051C0 |  |  | Yes, Refer to Our offer, Rev E |  |  | TBD
| Power supply unit |  | Based on Technical Offer , Shall be specified by Vendor |  |  |  |  | SE5009 |  |  | Yes, Refer to Our offer, Rev E |  |  | TBD
U-3 | Supporting doc / Catalogue including components technical spec. |  | As requested |  |  |  |  | Confirmed |  |  | confirmed |  |  | TBD
U-4 | Guarantee and Warranty |  | According to Project Specification |  |  |  |  | Confirmed |  |  | 12 month from the date of successful start-up or 18 month from the date of transportation whichever occurs first |  |  | TBD
U-5 | Delivery time of total system |  | Based on Technical Offer , Shall be specified by Vendor |  |  |  |  | 180 Days |  |  | 4 months |  |  | TBD
U-6 | Price validity date |  | based on Technical Offer , Shall be specified by Vendor |  |  |  |  | 90 Days |  |  | 3 months |  |  | TBD
U-7 | Documentation |  | Requisition |  |  |  |  | Confirmed |  |  | Yes, Refer to Our offer, Rev E |  |  | TBD
U-8 | Country of origin for major components |  | Contract (Shall be specified by vendor) |  |  |  |  | Europe |  |  | Germany |  |  | TBD
U-9 | Material Test Certificate |  | Requisition |  |  |  |  | Confirmed |  |  | confirmed |  |  | TBD
U-10 | SIL |  | Yes |  |  |  |  | Confirmed | [5 empty] | Confimed
V | CYBER SECURITY
V-1 | In Compliance With Cyber Security Requirements |  | As per Projec Specifications |  |  |  |  | Confirmed |  |  | Confirmed |  |  | Confirmed
X | Deviations / Alternatives
X-1 | Deviations (if any) |  | signed and stamped |  |  |  |  | Confirmed |  |  | No Deviations |  |  | AFTER MEETING
X-2 | Manufacturer's Location |  | - |  |  |  |  | Karaj/Payam Airport |  |  | tehran |  |  | KARAJ
Z | PROPOSAL DOCUMENTATION
Z-1 | Quality plan / ITP / FAT |  | shall be submitted |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
Z-2 | Standard certificates |  | shall be submitted |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
Z-3 | Confirmed scope of work & scope of supply as per MR |  | shall be submitted |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
Z-4 | Filled TBE |  | shall be submitted |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
Z-5 | Summary sheets |  | shall be submitted |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
Z-6 | Sub vendor list (if any) |  | shall be submitted |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
Z-7 | Reference list |  | shall be submitted |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
Z-8 | Firm price(s) by item Hardware – Console, Process Controller, I/O module for each type, Module, Cabinet with accessory, Power Supply, Console Aux. device, etc. |  | shall be submitted |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
Z-9 | Catalogues |  | shall be submitted |  |  |  |  | Confirmed |  |  | confirmed |  |  | Confimed
General Technical acceptance of Quotation | [7 empty] | ACCEPTED |  |  | ACCEPTED |  |  | ACCEPTED
Notes:
- Each item to be specified or confirmed by vendor, deviation to be colored red.