| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| PROCESS ELECTRICAL LOAD LIST نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |  |
| D05 |  | SEP.2023 | AFC | M.Aryafar | M.Fakharian | A.M.Mohseni |  |
| D04 |  | JUL.2023 | AFC | M.Aryafar | M.Fakharian | A.M.Mohseni |  |
| D03 |  | JAN.2023 | IFA | M.Aryafar | M.Fakharian | M.Mehrshad |  |
| D02 |  | AUG.2022 | IFA | M.Aryafar | M.Fakharian | M.Mehrshad |  |
| D01 |  | MAR.2022 | IFA | M.Aryafar | M.Fakharian | M.Mehrshad |  |
| D00 |  | JAN.2022 | IFC | M.Aryafar | M.Fakharian | M.Mehrshad |  |
| Rev. |  | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | CLIENT Approval |
| Class: 1 |  |  | CLIENT Doc. Number: F0Z-708808 |  |  |  |  |
| Status: |  | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for CLIENT Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 | D05 |  | PAGE | D00 | D01 | D02 | D03 | D04 | D05 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X | X | X | X | X | X |  | 66 |  |  |  |  |  |  |
| 2 | X | X | X | X | X | X |  | 67 |  |  |  |  |  |  |
| 3 | X |  |  |  |  |  |  | 68 |  |  |  |  |  |  |
| 4 | X |  |  |  |  |  |  | 69 |  |  |  |  |  |  |
| 5 | X |  |  |  |  |  |  | 70 |  |  |  |  |  |  |
| 6 | X | X | X | X | X | X |  | 71 |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  | 72 |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  | 73 |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  | 74 |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  | 75 |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  | 76 |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  | 77 |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  | 78 |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  | 79 |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  | 80 |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |  | 81 |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  | 82 |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |  | 83 |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |  | 84 |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |  | 85 |  |  |  |  |  |  |
| 21 |  |  |  |  |  |  |  | 86 |  |  |  |  |  |  |
| 22 |  |  |  |  |  |  |  | 87 |  |  |  |  |  |  |
| 23 |  |  |  |  |  |  |  | 88 |  |  |  |  |  |  |
| 24 |  |  |  |  |  |  |  | 89 |  |  |  |  |  |  |
| 25 |  |  |  |  |  |  |  | 90 |  |  |  |  |  |  |
| 26 |  |  |  |  |  |  |  | 91 |  |  |  |  |  |  |
| 27 |  |  |  |  |  |  |  | 92 |  |  |  |  |  |  |
| 28 |  |  |  |  |  |  |  | 93 |  |  |  |  |  |  |
| 29 |  |  |  |  |  |  |  | 94 |  |  |  |  |  |  |
| 30 |  |  |  |  |  |  |  | 95 |  |  |  |  |  |  |
| 31 |  |  |  |  |  |  |  | 96 |  |  |  |  |  |  |
| 32 |  |  |  |  |  |  |  | 97 |  |  |  |  |  |  |
| 33 |  |  |  |  |  |  |  | 98 |  |  |  |  |  |  |
| 34 |  |  |  |  |  |  |  | 99 |  |  |  |  |  |  |
| 35 |  |  |  |  |  |  |  | 100 |  |  |  |  |  |  |
| 36 |  |  |  |  |  |  |  | 101 |  |  |  |  |  |  |
| 37 |  |  |  |  |  |  |  | 102 |  |  |  |  |  |  |
| 38 |  |  |  |  |  |  |  | 103 |  |  |  |  |  |  |
| 39 |  |  |  |  |  |  |  | 104 |  |  |  |  |  |  |
| 40 |  |  |  |  |  |  |  | 105 |  |  |  |  |  |  |
| 41 |  |  |  |  |  |  |  | 106 |  |  |  |  |  |  |
| 42 |  |  |  |  |  |  |  | 107 |  |  |  |  |  |  |
| 43 |  |  |  |  |  |  |  | 108 |  |  |  |  |  |  |
| 44 |  |  |  |  |  |  |  | 109 |  |  |  |  |  |  |
| 45 |  |  |  |  |  |  |  | 110 |  |  |  |  |  |  |
| 46 |  |  |  |  |  |  |  | 111 |  |  |  |  |  |  |
| 47 |  |  |  |  |  |  |  | 112 |  |  |  |  |  |  |
| 48 |  |  |  |  |  |  |  | 113 |  |  |  |  |  |  |
| 49 |  |  |  |  |  |  |  | 114 |  |  |  |  |  |  |
| 50 |  |  |  |  |  |  |  | 115 |  |  |  |  |  |  |
| 51 |  |  |  |  |  |  |  | 116 |  |  |  |  |  |  |
| 52 |  |  |  |  |  |  |  | 117 |  |  |  |  |  |  |
| 53 |  |  |  |  |  |  |  | 118 |  |  |  |  |  |  |
| 54 |  |  |  |  |  |  |  | 119 |  |  |  |  |  |  |
| 55 |  |  |  |  |  |  |  | 120 |  |  |  |  |  |  |
| 56 |  |  |  |  |  |  |  | 121 |  |  |  |  |  |  |
| 57 |  |  |  |  |  |  |  | 122 |  |  |  |  |  |  |
| 58 |  |  |  |  |  |  |  | 123 |  |  |  |  |  |  |
| 59 |  |  |  |  |  |  |  | 124 |  |  |  |  |  |  |
| 60 |  |  |  |  |  |  |  | 125 |  |  |  |  |  |  |
| 61 |  |  |  |  |  |  |  | 126 |  |  |  |  |  |  |
| 62 |  |  |  |  |  |  |  | 127 |  |  |  |  |  |  |
| 63 |  |  |  |  |  |  |  | 128 |  |  |  |  |  |  |
| 64 |  |  |  |  |  |  |  | 129 |  |  |  |  |  |  |
| 65 |  |  |  |  |  |  |  | 130 |  |  |  |  |  |  |

CONTENTS

1.0	INTRODUCTION	4

2.0	Scope	4

3.0	NORMATIVE REFERENCES	5

3.1	The Project Documents	5

3.2	ENVIRONMENTAL DATA	5

4.0	ELECTRICAL CONSUMPTION	6

- INTRODUCTION

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO). Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

GENERAL DEFINITION

The following terms shall be used in this document.

| CLIENT: | National Iranian South Oilfields Company (NISOC) |
| --- | --- |
| PROJECT: | Binak Oilfield Development – Surface Facilities; New Gas Compressor Station |
| EPD/EPC CONTRACTOR: | Petro Iran Development Company (PEDCO) |
| EPC CONTRACTOR: | Joint Venture of : Hirgan Energy – Design & Inspection(D&I) Companies |
| VENDOR: | The firm or person who will fabricate the equipment or material. |
| EXECUTOR: | Executor is the party which carries out all or part of construction and/or commissioning for the project. |
| THIRD PARTY INSPECTOR (TPI): | The firm appointed by EPC CONTRACTOR and approved by GC & CLIENT (in writing) for the inspection of goods. |
| SHALL: | Is used where a provision is mandatory. |
| SHOULD: | Is used where a provision is advisory only. |
| WILL: | Is normally used in connection with the action by CLIENT rather than by an EPC/EPD CONTRACTOR, supplier or VENDOR. |
| MAY: | Is used where a provision is completely discretionary. |

- Scope

The purpose of this document is to provide summary of process electrical loads for BINAK Gas Compressor Station”.

- NORMATIVE REFERENCES

## The Project Documents

- BK-GNRAL-PEDCO-000-PR-DC-0001	Process Design Criteria

- BK-GNRAL-PEDCO-000-PR-DB-0001	Process Basis Of Design

- BK-GCS-PEDCO-120-PR-UF-0001		Utility Flow Diagrams (UFD)

- BK-GCS-PEDCO-120-PR-PI-0002~0025	P&ID

- BK-GCS-PEDCO-120-PR-PF-0001		Process Flow Diagram (PFD)

## ENVIRONMENTAL DATA

Refer to "Process Basis of Design; Doc. No. BK-GNRAL-PEDCO-000-PR-DB-0001".

D05

ELECTRICAL CONSUMPTION

| No. | ITEM No. | SERVICE | C / I | Configuration | Emergency | N/S | Efficiency |  | POWER (EACH) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  | BHP (kW) |
| 1 | AC-2101A | 1st Stage Air Coolers | C | 1 | - | N | - |  | 2 x 5.5 (NOTE1) |
| 2 | AC-2101B | 1st Stage Air Coolers | C | 1 | - | N | - |  | 2 x 5.5 (NOTE1) |
| 3 | AC-2101C | 1st Stage Air Coolers | C | 1 | - | S | - |  | 2 x 5.5 (NOTE1) |
| 4 | AC-2102 A | 2nd Stage Air Coolers | C | 1 | - | N | - |  | 2 x 5.5 (NOTE1) |
| 5 | AC-2102B | 2nd Stage Air Coolers | C | 1 | - | N | - |  | 2 x 5.5 (NOTE1) |
| 6 | AC-2102C | 2nd Stage Air Coolers | C | 1 | - | S | - |  | 2 x 5.5 (NOTE1) |
| 7 | C-2101 A/B/C C-2102 A/B/C | 1st & 2nd Stage Gas Compressor Package + Other Consumption | C | 2+1 | - | 2N+S | - |  | 1070 (Each) |
| 8 | PK-C-2203 A/B | Instrument & Plant Air Package | C | 1+1 | E | N+S | - |  | Motor power:75(Each) (NOTE1) |
| 9 | PK-C-2204 | Air compressor for N2 Package | C | 1 | - | N | - |  | Motor power:75(Each) Heat exchanger(if any):4.5 Chilling Unit(if any):4 (NOTE1) |
| 10 | PK-2201 | LP Flare Package (Including blower for smokeless Flare) | C | 1 | - | N | - |  | 30 (NOTE1) |
| 11 | IG-2201 | LP Flare Ignition Package | I | 1 | E | N | - |  | 1 (NOTE1) |
| 12 | PK-2207 | Corrosion Inhibitor Package | C | 1 | - | N | - |  | 3.5 (NOTE1) |
| 13 | PK-2208 | Methanol Injection Package | DELETED |  |  |  |  |  |  |
| 14 | PK‐2101 | Dehydration Package | C | 1 | - | N |  | - | 2 x2.2 (NOTE1) |
| 15 | P-2203A/B | Sump Pump | I | 1+1 | E | N+S |  | 29% | 1.1 (Each) |
| 16 | P-2202 A/B | Closed Drain Pumps | I | 1+1 | E | N+S |  | 17% | 3.7(Each) |
| 17 | P-2101A/B | Slug Pumps | I | 1+1 | E | N+S |  | 43% | 14(Each) |
| 18 | P-2302 A/B | Fire Water Jockey Pumps | I | 1+1 | - | N+S |  | 29% | Rated power =14.8 Motor Power =18.5 |
| 19 | P-2301 A | Fire Water electric Pump | I | 1 | - | N |  | 72% | Rated power =180.5 Motor Power =250 |
| 20 | P-2301 B | Fire Water Pumps-Diesel Engine Driven |  | 1 |  |  |  | 72% | Rated Power:180.5 Motor Power:308 |
| 21 | P-2209 | Potable Water Pumps | I | 1 | - | N |  | 32% | 1.3 |
| 22 | P-2206 | Diesel Oil Pump | I | 1 | - | N |  | 33% | 1 |
| 23 | P-2201A/B | LP Flare K.O. Drum Pumps | I | 1+1 | E | N+S |  | 15% | 0.6 (Each) |
| 24 | P-2103 A/B | Glycol Transfer Pumps | I | 1+1 | - | N+S |  | 31% | 1.5 |
| 25 | P-2102 | Glycol Manual Pump | I | 1 | - | N |  | 31% | 0.4(Each) |
| 26 | P-2104 | Glycol Drain Pump | I | 1 | - | N |  | 22% | 0.8 |
| 27 | - | MOV | I | 2 | - | N |  | - | 2(NOTE1) |
| 28 | Electrical tracing 1st Stage | 1st Stage Compressors | C | 2+1 | %85 | 2N+S |  | - | 0.227 |
| 29 | Electrical tracing 2nd Stage | 2nd Stage Compressors | C | 2+1 | %85 | 2N+S |  | - | 2.625 |

NOTE 1: Will be finalized by vendor.

C: Continues/ E: Emergency Load/ I:  Intermittent/ N: Normal Load/ S: Standby