## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-HV-CN-0004 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2526 |  |  | Transmital Date: 1/1/2024
Document Title: HVAC Calculation Note For Extension of Existing Control Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-HV-TR-2526 |  |  | Transmital Date: 1/1/2024
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-HV-CN-0004_D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
HVAC comments :
1 | دمای اتاق باتری می بایست طبق استاندارد 24 درجه سانتیگراد می باشد و نیاز به سرمایش دارد. |  | 1402-2294-487095 | 1402/11/25 | با توجه تغییر سیستم HVAC ساختمان کنترل و نقطه نظرات مطرح شده، محاسبات مربوطه به طور کل مورد بازنگری قرار گرفت.
2 | فضای Locker در فایل محاسبات در بخش Space نرم افزار HAP تعریف نشده است. |  | 1402-2294-487095 | 1402/11/25
3 | فضای Locker نیاز به تعویض هوا و هواکش دارد. |  | 1402-2294-487095 | 1402/11/25
4 | طبق استاندارد IPS-E-AR-160 فضای UPS و اتاق باتری نیاز به دستگاه سرمایش ذخیره (1+1) دارد. |  | 1402-2294-487095 | 1402/11/25
5 | صفحه 34 از 36 برای اتاق باتری طبق پیوست 6 استاندارد IPS-E-AR-160 تعویض هوا معادل 10-12 بار در ساعت در نظر گرفته شود. |  | 1402-2294-487095 | 1402/11/25
6 | در قسمت Space Input Data نیاز است بخشهای Electrical Equipment , Over Head Lighting و Infiltration بازنگری گردد. مقدار Over Head Lighting معادل 20 w/m2 و مقدار توجه به تعداد رایانه ها، یخچال و چاپگرهای داخل هر فضا تعریف گردد. |  | 1402-2294-487095 | 1402/11/25
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: