## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-HV-CN-0004 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2526 |  |  | Transmital Date: 1/1/2024
Document Title: HVAC Calculation Note For Extension of Existing Control Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-HV-TR-2526 |  |  | Transmital Date: 1/1/2024
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-HV-CN-0004_D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
HVAC comments :
1 | Find the attached file . |  | BK-SUR-ENG-HVC-02-08942 | 2024-01-13 | HVAC Calculation For Extension of Existing Control Building Totally Revised.
Electrical comments :
1 | تعداد دفعات تعويض هواي اتاق باطري در هر ساعت برابر 6 در نظر گرفته شده است. اين عدد توسط IPS-E-EL-100 برابر 12 پيشنهاد شده است. لازم است تعداد دفعات تعويض هواي مورد نياز با توجه به حجم اتاق و سايز باطري ها به كمك نرم افزار BasiCs توسط بخش برق محاسبه شده و در محاسبات باطري آورده شود و نتيجه در اختيار بخش HVAC جهت سايزينگ فن قرار داده شود. |  | BK-SUR-ENG-HVC-02-08942 | 2024-01-13 | تعداد دفعات تعويض هواي اتاق باطري در هر ساعت برابر 10 در ساعت (بر اساس مدرک Hvac & Plumbing Design Criteria) در نظر گرفته شد. همچنین محاسبات تعداد دفعات تعويض هواي مورد نياز با توجه به حجم اتاق و سايز باطري ها به كمك نرم افزار BasiCs توسط بخش برق محاسبه شده و نتایج به پیوست ارائه می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: