## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0017 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2637 |  |  | Transmital Date: 3/12/2024
Document Title: P&ID - Close Drain System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-2637 |  |  | Transmital Date: 3/12/2024
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-PI-0017_D08 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | پیش تر طی بنامه شماره 335919 مورخ 1402.08.22 به اطلاع آن پیمانکار رسانده شده که شیب خط CDH-112- 0030-AN07-6"-PT می بایست 1:100 لحاظ گردد. |  | 1403-2294-82570 | 1403/03/01 | مورد تایید است.
2 | برای پمپ ها Vent در نظر گرفته شود. |  | 1403-2294-82570 | 1403/03/01 | مورد تایید است.
3 | شیر خروجی گاز به سمت شبکه فلر می بایست به صورت باز نمایش داده شود. |  | 1403-2294-82570 | 1403/03/01 | مورد تایید است.
3 | با توجه به در جریان بودن مذاکرات و تصمیم گیری در خصوص تغییر نوع پمپ ها از حالت افقی به عمودی، مدرک می بایست با توجه به گزینه نهایی مجددا ارسال گردد.نامه شماره )340600 مورخ 1402/08/24) |  | 1403-2294-82570 | 1403/03/01 | مورد تایید است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: