## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0020 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2637 |  |  | Transmital Date: 3/12/2024
Document Title: P&ID - LP Flare System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-2637 |  |  | Transmital Date: 3/12/2024
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-PI-0020_D08 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به در جریان بودن مذاکرات و تصمیم گیری در خصوص تغییر نوع پمپ ها از حالت افقی به عمودی، مدرک می بایست با توجه به گزینه نهایی مجدد ارسال گردد.(نامه شماره 340600 مورخ 1402.08.24 ) |  | 1403-2294-82570 | 1403/03/01 | اعمال گردید.
2 | پیمانکار می بایست علت درج نوت 15 را توضیح دهد. در حال حاضر با برداشتی که از مدرک حاصل می شود روشن شدن دمنده ها فقط در شرایط (ESD 1A-SHUT DOWN WITH DEPRESSURIZIN( رخ می دهد در صورتی که فلر ها می بایست در کل بازه جریان تخلیه گاز به مشعل بدون دود کار کنند و این مهم می بایست توسط دمنده های هوا ایجاد گردد. |  | 1403-2294-82570 | 1403/03/01 | نوت 15 اصلاح گردید.
3
4
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: