## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0011 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2325 |  |  | Transmital Date: 8/29/2023
Document Title: Calculation Note for Capacitor Banks |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-2325 |  |  | Transmital Date: 8/29/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-CN-0011_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در این مقطع از پروژه لازم است اطلاعات نهایی سازنده الکتروموتورهای C-2101A ارائه و مبنای محاسبات قرار گیرد. لذا داده های Total Active & Reactive Peak Load Power همراه مستندات ارائه گردد. |  | 1402-2294-393269 | 1402/09/28 | بر اساس ویرایش سوم از مدرک داده بر گه موتور کمپرسور، مدرک محاسباتی به روزرسانی گردید.
2 | بر اساس داده برگ سازنده الکتروموتور پروژه، جریان بی باری موتور 30.8 آمپر در محاسبات در نظر گرفته شود. |  | 1402-2294-393269 | 1402/09/28 | اعمال گردید.
3 | در مقطع تأمین کالا لازم است محاسبات توسط سازنده تابلو بر اساس آخرین ویرایش مدرک لیست بارهای پروژه، ملاحظات استانداردی و پروژه صحه گذاری گردد. |  | 1402-2294-393269 | 1402/09/28 | در مقطع عقد قرارداد، سازنده می بایست بر اساس لیست بار الکتریکی، محاسبات بانک خازنی را مورد بازنگری و ویرایش قرار دهد.
4 | به دلیل عدم ارائه اطلاعات الکتریکال مربوط به کلیه سازندگان در این مقطع از پروژه، بدیهی است پس از دریافت مدارک سازندگان می بایست نسبت به اصلاح مدرک اقدام گردد. |  | 1402-2294-393269 | 1402/09/28 | لیست بارهای الکتریکی اصلاح گردیده است. بر همین اساس بارهای موتوری شرکت هوایار نهایی شده است.
5 | تغییرات متناظر با هر گونه تغییر در مدرک لیست بارها، می بایست در مدرک اعمال گردد. |  | 1402-2294-393269 | 1402/09/28 | اعمال گردید.
6 | توضیحات مندرج در بخش عمومی رعایت گردد. |  | 1402-2294-393269 | 1402/09/28 | اعمال می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: