## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0003 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1723 |  |  | Transmital Date: 12/24/2022
Document Title: Existent MV Switchgear Expansion Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-1723 |  |  | Transmital Date: 12/24/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-SL-0003_D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در نقشه می بایست LCS مربوط به الکتروپمپ آتش نشانی و CT آن نمایش داده شود. |  | 1401-2294-422761 | 1401/11/05 | مطابق با صورتجلسه مورخ 30 اردیبهشت 1403، یک عدد CT یک به یک بر روی موتور آتش نشانی و کمپرسورهای اصلی لحاظ گردید.
2 | کابل RDT، و ارتباط به رله مربوطه در فیدر الکتروموتور کمپرسور گاز نمایش داده شود. |  | 1401-2294-422761 | 1401/11/05 | کابل RTD که مربوط به کد رله 49T می باشد، از رله برداشته شد و به UCP انتقال یافت.به نوت 8 از مدرک مراجعه شود.
3 | سطح مقطع کابلهای قدرت پس از نهایی سازی مدرک سایزینگ کابل می بایست در مدرک نمایش داده شود |  | 1401-2294-422761 | 1401/11/05 | مطابق با صورتجلسه مورخ 30 اردیبهشت 1403، مدرک سایزینگ کابل مورد تأیید می باشد
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: