## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0007 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2325 |  |  | Transmital Date: 8/29/2023
Document Title: Capacitor Banks Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-2325 |  |  | Transmital Date: 8/29/2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-SL-0007_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised base on comments on "Calculation Note for Capacitor Banks" document such as MV capacitor bank for fire water pump. (If Required) |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | مدارک محاسباتی مورد بازنگری قرار گرفت و آخرین تغییرات در مدارک لحاظ گردید. لازم به ذکر است در صورت هرگونه تغییردر مدارک، موارد جدیدی در نظر گرفته خواهد شد. |  |  | Noted and Closed.
2 | According to our telephone conversation, Short circuit level shall be modified after submitting network study especially for LV capacitor bank. (If required) |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | مطابق با تغییرات در مدرک دیتاشیت و بر اساس مطالعات شبکه، سطح اتصال کوتاه در نظر گرفته شده است. |  |  | Noted and Closed.
3 | Voltage sample for APFR shall be shown in single line diagram. |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | با توجه به اینکه Automatic Power Factor Regulator تجهیز تنظیم کننده بانک خازن است، در لجند مدرک اضافه گردید. |  |  | See below item 14-1.
4 | Normal/Fault signal lamp shall be considered for outgoing feeders. |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | چراغ سیگنال روشن/خاموش و خطا برای خروجی ها اضافه گردید. |  |  | Noted and Closed.
5 | Voltage protection (27/47/59) shall be added for incoming feeder. (For LV cpacitor bank.) |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | یک عدد PHC (کنترل فاز) برای در نظر گرفتن رله های ولتاژی اضافه گردید. |  |  | Noted and Closed.
6 | Earth switch and surge arrester shall be added for MV capacitor bank. |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | اضافه گردید |  |  | Noted and Closed.
7 | Signal lamp for phases shall be added for incoming feeder. |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | چراغ سیگنال های هر فاز در کلید ورودی نشان داده شده است. |  |  | Noted and Closed.
8 | It should be clarified about how to supply the control voltage in the capacitor bank panel. |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | نوت شماره 7 هم در مدرک دیاگرام تک خطی و هم در مدرک داده برگ بانک خازنی با موضوع در نظر گرفتن یک عدد ترانس ایزوله خشک توسط سازنده تابلو جهت استفاده در مدار کنترلی اضافه گردید. |  |  | Noted and Closed.
9 | It seems the signal lamp for incoming CB shall be modified base on type of MCCB CB. |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | چراغ سیگنال های مورد نیاز تابلو اضافه گردیده است. |  |  | Noted and Closed.
10 | APFR abbreviation shall be added on legend page. |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | در لجند مدرک اضافه گردیده است. |  |  | Noted and Closed.
11 | Incoming feeder current rating shall be compatible with outgoing feeder for capacitor bank in LV switchgear. |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | کلید ورودی به صورت 4 پل و با ظرفیت 315 آمپر در نظر گرفته شده است. |  |  | Noted and Closed.
12 | The symbols in SLD shall be selected base on legend pages, for example incoming CB is MCCB, but the symbol in SLD is not corrected. |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | مطابق با سیمبل پروژه اصلاح گردید. |  |  | Noted and Closed.
13 | Following note shall be added: -All capacitors shall be provided with a discharge resistor, characteristics of which shall be specified by vendor. Capacitors must discharge to a residual voltage less than 75v within 3 minutes. -The capacitor bank rating power should be considered in 400v/11KV, but capacitor rating voltage should be 440v/12KV. |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | اعمال گردید. |  |  | Noted and Closed.
14 | According to our telephone conversation, following items shall be rechecked and modified or added: |  | BK-SUR-ENG-ELE-01-05478 | 2022-08-17 |  |  |  | Noted and Closed.
14-1 | See above item 3: Voltage sample for APFR has not been shown. |  | BK-SUR-ENG-ELE-01-05478 | 2022-08-17 | اعمال گردید. |  |  | Noted and Closed.
14-2 | Note 6 is not apllicable for GCS and shall be deleted. |  | BK-SUR-ENG-ELE-01-05478 | 2022-08-17 | حذف گردید. |  |  | Noted and Closed.
14-3 | VCB for MV capacitor bank shall be deleted. |  | BK-SUR-ENG-ELE-01-05478 | 2022-08-17 | حذف گردید. |  |  | Noted and Closed.
14-4 | Rated power of MV capacitor bank shall be modified base on latest revision of capacitor bank calculation document. (500KVAR) |  | BK-SUR-ENG-ELE-01-05478 | 2022-08-17 | بر اساس آخرین محاسبات بانک خازنی، توان راکتیو 360 کیلووار خواهد بود. |  |  | Noted and Closed.
14-5 | Note 8 shall be applicable for both MV and LV capacitor bank base on IPS-M-EL-180(2). (10min for MV capacitor bank). |  | BK-SUR-ENG-ELE-01-05478 | 2022-08-17 | اعمال گردید. |  |  | Noted and Closed.
14-6 | CT&PT accuracy class shall be considered class 1. |  | BK-SUR-ENG-ELE-01-05478 | 2022-08-17 | اعمال گردید. |  |  | Noted and Closed.
15 | This document shall be revised based on comments on "Calculation Note for Capacitor Banks" document. |  | BK-SUR-ENG-ELE-02-08384 | 2023-09-03 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: