## Cover
| NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
| شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه
| 9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0010 | D02
.
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR ON/OFF & SHUTDOWN VALVES نگهداشت و افزایش تولید میدان نفتی بینک
| D02 |  | AUG.2024 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Sadeghian
| D01 |  | OCT.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
| D00 |  | MAY.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
| Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: | CLIENT Approval
| Class: 1 |  |  |  | CLIENT Doc. Number: F9Z-708931
| status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
| شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه
| 9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0010 |  | D02
REVISION RECORD SHEET
| Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 | D02 | D03 | D04
| 1 | X | X | X | [5 empty] | 65
| 2 | X | X | X | [5 empty] | 66
| 3 | X | X | X | [5 empty] | 67
| 4 | X | X | X | [5 empty] | 68
| 5 | X | X | X | [5 empty] | 69
| 6 | X | X | X | [5 empty] | 70
| 7 | X | X | X | [5 empty] | 71
| 8 | X | X | X | [5 empty] | 72
| 9 | X | X | X | [5 empty] | 73
| 10 | X | X | X | [5 empty] | 74
| 11 | X | X | X | [5 empty] | 75
| 12 | X | X | X | [5 empty] | 76
| 13 | X | X | X | [5 empty] | 77
| 14 | X | X | X | [5 empty] | 78
| 15 | X | X | X | [5 empty] | 79
| 16 | X | X | X | [5 empty] | 80
| 17 | X | X | X | [5 empty] | 81
| 18 | X | X | X | [5 empty] | 82
| 19 | X | X | X | [5 empty] | 83
| 20 | X | X | X | [5 empty] | 84
| 21 | X | X | X | [5 empty] | 85
| 22 | X | X | X | [5 empty] | 86
| 23 | X | X | X | [5 empty] | 87
| 24 | X | X | X | [5 empty] | 88
| 25 | X | X | X | [5 empty] | 89
| 26 | X | X | X | [5 empty] | 90
| 27 | X | X | X | [5 empty] | 91
| 28 | X | X | X | [5 empty] | 92
| 29 | X | X | X | [5 empty] | 93
| 30 | X | X | X | [5 empty] | 94
| 31 | X | X | X | [5 empty] | 95
| 32 | X | X | X | [5 empty] | 96
| 33 | X | X | X | [5 empty] | 97
| 34 | X | X | X | [5 empty] | 98
| 35 | X | X | X | [5 empty] | 99
| 36 | X | X | X | [5 empty] | 100
| 37 | X | X | X | [5 empty] | 101
| 38 |  |  | X | [5 empty] | 102
| 39 |  |  | X | [5 empty] | 103
| 40 |  |  | X | [5 empty] | 104
| 41 |  |  | X | [5 empty] | 105
| 42 |  |  | X | [5 empty] | 106
| 43 |  |  | X | [5 empty] | 107
| 44 |  |  | X | [5 empty] | 108
| 45 | [8 empty] | 109
| 46 | [8 empty] | 110
| 47 | [8 empty] | 111
| 48 | [8 empty] | 112
| 49 | [8 empty] | 113
| 50 | [8 empty] | 114
| 51 | [8 empty] | 115
| 52 | [8 empty] | 116
| 53 | [8 empty] | 117
| 54 | [8 empty] | 118
| 55 | [8 empty] | 119
| 56 | [8 empty] | 120
| 57 | [8 empty] | 121
| 58 | [8 empty] | 122
| 59 | [8 empty] | 123
| 60 | [8 empty] | 124
| 61 | [8 empty] | 125
| 62 | [8 empty] | 126
| 63 | [8 empty] | 127
| 64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001
|  | Instrument & Control System Design Criteria | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0002
|  | Specification For Hazardous Area Classification | [6 empty] | BK-GNRAL-PEDCO-000-SA-SP-0002
|  | Specification For On-off /Shut Down Valves(ESDV/MOV) | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0006
|  | Specification For Painting | [6 empty] | BK-GNRAL-PEDCO-000-PI-SP-0006
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002
D02

## Notes
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
| شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
| 9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
GENERAL NOTES:
1. Calculations shall be provided for each completely piped actuated valve assembly (including solenoid valve), the stroking times i.e. to close and to open.
2. The duty, failure action and stroke time shall all be approved by the Purchaser.
3. The actuator shall be designed to operate the valve through its full stroke.
4. The maximum valve stroking time to achieve the safety position shall be defined according to size of the body (5 seconds for body until 4", 1 second per inch for body greater than 4"). The maximum fully stroke time shall be 10 seconds.
5. The piping indicates corrosion allowance selected as per document "Piping & Pipeline Material Specification, No. " BK-GCS-PEDCO-120-PI-SP-0001 "
6. Hydro-test duration shall be in accordance with API 6D.
7. All ball valves shall be fitted with suitable 'end of travel' stops at the fully open and fully closed positions and a local position indicator . The design shall prevent the ingress of foreign material and corrosion products which would impair the operation of the stops. Devices capable of locking the valves in their safe position ( ESDV in open or closed position ) shall be provided for maintenance and shall be vendor's standard proven design.
8. Vendor shall guarantee and demonstrate the required stroking speed, during the Functional Test (FAT).
9. All accessories shall be mounted, together with solenoid valve, etc, on a 316SS sub-plate. Tubing shall be suitably sized TP 316L stainless steel with stainless steel double ferrule compression fittings
10. Solenoid valve shall be selected in accordance with low power type.
11. All on/off valves shall be preferably fitted with single acting, spring return pnumatic actuators, completed with mounting kit. Also Partial Stroking test or pilot valve to be considered.
12. The actuator shall be fail safe in operation (as specified in data sheets) in loss of electrical signal or loss of air supply.
13. The spring return actoator shall be "pre stressed".
14. Pneumatic actuators will be sized on the basis of a minimum safety factor of 1.5 and a minimum air pressure of 3 Bar g. The valve actuator torque shall be in excess of the required valve torque under all operating conditions.
15.All actuators and accessories shall be clearly and permanently identified by nameplate. the nameplate shall be in stainless steel and affixed to the VALVE, actuator and accessories.
16 - Environmental condition for field instrumentation of Binak Oilfield shall be considered as per the followings:
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: 5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: 50 (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % DB FOR Winter HVAC Design: 6 °C
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0
17 - Material Test Certificate and calibration Certificate for all transmitters to be submitted by Vendor.
18 - Flow direction shall be permanently and clearly indicated on the valve body.
19- External grounding shall be provided for each solenoid valve.
20- BDV’s shall have a minimum body size of 2” with tight shutoff (ANSI B16.104, class VI), air volume tanks for larger valves and should be sized for three full open/ closed operations at 3-barg instrument air pressure.
21- Valves in safety related services should have been fire tested and certification to be provided by Vendor.
22- Seat rings shall be spring loaded and so designed that line pressure will assist in sealing round the ball.
23- Valve stem extension shall be detachable for easy replacements.
24- At least two stem seals shall be provided with facility for injection of secondary sealant and with stainless steel fittings.
25- Stem seal shall be replaceable while the valve is in closed operation position.
26- Short stroke single acting pneumatic piston actuators shall preferably be used on emergency shutdown service.
27- Body of all On/Off Valves except ss316 body material, shall be painted with white color. Also actuator of ESDV and BDV valves shall be painted with Red color as well as actuator of XV valves shall be painted by Blue color.
D02

## ESDV-2101
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
Shut Down Valve
TAG NO: |  | ESDV-2101 |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0002_D08 | [6 empty] | SERVICE: | Gas Compression Inlet Gas Pipeline (Binak)
FLUID STATE: | PROCESS GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | 7220.4928 | 6564.084 | 1969.23 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 7.5 | 7.5 | 7.5 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 7.5 | 7.5 | 7.5 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 18.2
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | 26.67~46.11 | 26.67~46.11 | 26.67~46.11 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 5.43 ~ 6.66 | 5.43 ~ 6.66 | 5.43 ~ 6.66 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.011 ~ 0.012 | 0.011 ~ 0.012 | 0.011 ~ 0.012 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 107.1 | 107.1 | 107.1 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 6" | 80 | CORROSION ALLOWANCE(mm) |  | 6 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting , Spring Return
|  |  | OUT | 6" | 80 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0001-AN07-6"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE | OUT |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE | OUT |  |  | 6" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. | OUT |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL | OUT |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL | OUT |  |  | ASTM A216 Gr. WCB | [5 empty] | 60 | TRAVELING TIME |  | 6 S
| 17 | LINER MATERIAL / ID | OUT |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 6" /300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 6" /300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | EZSC-2101 / EZSO-2101
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | ESOV-2101 | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | Yes
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | No | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUAL PNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## ESDV-2102
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
Shut Down Valve
TAG NO: |  | ESDV-2102 |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0003-D08 | [6 empty] | SERVICE: | Gas Compression Inlet Gas Pipeline (Golkhari)
FLUID STATE: | PROCESS GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | 12395.9313 | 11269.02 | 3380 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 7.5 | 7.5 | 7.5 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 7.5 | 7.5 | 7.5 | 90
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | -
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | 15.5 ~ 32 | 15.5 ~ 32 | 15.5 ~ 32 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 6.19 ~6.21 | 6.19 ~6.21 | 6.19 ~6.21 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.011 | 0.011 | 0.011 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 103.1 | 103.1 | 103.1 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 8" | 100 | CORROSION ALLOWANCE(mm) |  | 6 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting , Spring Return
|  |  | OUT | 8" | 100 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0001-FN07-8"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 8" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A216 Gr. WCB | [5 empty] | 60 | TRAVELING TIME |  | 9 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 8" /600# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 8" /600# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | EZSC-2102 / EZSO-2102
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | Forged, 13% chromium steel |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | ESOV-2102 | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | Yes
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | No | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUAL PNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## ESDV-2113
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
Shut Down Valve
TAG NO: |  | ESDV-2113 |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0005-D08 | [6 empty] | SERVICE: | Gas Compression Inlet Knock Out Drum to Closed Drain
FLUID STATE: | CLOSED DRAIN HYDROCARBON |  |  | PHASE: |  | Lliquid | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | 1119.5286 | 1017.7533 | 305.326 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 5.3 | 5.3 | 5.3 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 5.3 | 5.3 | 5.3 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 13.9
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | 19.02~36.9 | 19.02~36.9 | 19.02~36.9 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 842.6~1012 | 842.6~1012 | 842.6~1012 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.69 ~ 1.026 | 0.69 ~ 1.026 | 0.69 ~ 1.026 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | 0.612 | 0.612 | 0.612 | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 221.4 | 221.4 | 221.4 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | SCH.10S | CORROSION ALLOWANCE(mm) |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting , Spring Return
|  |  | OUT | 2" | SCH.10S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | CDH-111-0019-AS00-2"-NP | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2" /300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2" /300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | EZSC-2113 / EZSO-2113
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | ESOV-2113 | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | No | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUAL PNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02
D02

## ESDV-2272
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
Shut Down Valve
TAG NO: |  | ESDV-2272 |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0022-D08 | [6 empty] | SERVICE: | Fuel Gas System
FLUID STATE: | FUEL GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | 556.3473 | 505.8 | 151.731 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 5.1 | 5.1 | 5.1 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 5.1 | 5.1 | 5.1 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 18.2
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | 37 | 37 | 37 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 5.77 | 5.77 | 5.77 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.011 | 0.011 | 0.011 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 94.66 | 94.66 | 94.66 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 3" | 80 | CORROSION ALLOWANCE(mm) |  | 6 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting , Spring Return
|  |  | OUT | 3" | 80 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0004-AN07-3"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 3" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A216 Gr. WCB | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 3" /300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 3" /300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | EZSC-2272 / EZSO-2272
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | ESOV-2272 | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | No | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUAL PNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## BDV-2110
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
Blow Down Valve
TAG NO: |  | BDV-2110 |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0005-D08 | [6 empty] | SERVICE: | Gas Compression Inlet Knock Out Drum to Flare Header
FLUID STATE: | PROCESS GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 5665.4 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 5.3 ~ 9 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 5.3 ~ 9 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 18.2
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 19 ~ 37.17 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 5.96 ~ 1012 | - | - | 0.011485
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.011 ~ 0.0115 | - | - | 0.011032
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | - | 94.65 | - | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 3" | 160 | CORROSION ALLOWANCE(mm) |  | 6 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 3 | 160 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0225-AN07-3"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Open
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 3" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A216 Gr. WCB | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 3"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 3"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | BZSC-2110 / BZSO-2110
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | BSOV-2110 , PSOV-2110 | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## BDV-2134A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
Blow Down Valve
TAG NO: |  | BDV-2134A |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0009-D08 (1/3) | [6 empty] | SERVICE: | 2nd Stage Gas Compression Suction Drums
FLUID STATE: | VENT GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 796.4 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 18.1~ 22 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 18.1~ 22 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 47.7
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 22 ~ 59.88 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 18.08~ 1011 | - | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.013 ~0.98 | - | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | - | 94.65 | - | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 80 | CORROSION ALLOWANCE(mm) |  | 6 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting , Spring Return
|  |  | OUT | 2" | 80 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0160A-CN05-2"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Open
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/ Floating Type | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A216 Gr. WCB | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2" /300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Declutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | No
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | BZSC-2134A / BZSO-2134A
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | BSOV-2134A , PSOV-2134A | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No |  |  |  |  | FIRE PROOF DESIGN | 91 | PASSIVE FIRE PROTECTION |  | No
| 47 | QUICK EXHUST |  |  |  | Yes | [5 empty] | 92 | API 6FA REQUIREMENTS |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | SIL 3 REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | No | [5 empty] | 94 | PARTIAL STROKING VALVE TEST |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## BDV-2134B
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
Blow Down Valve
TAG NO: |  | BDV-2134B |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0009-D08 (2/3) | [6 empty] | SERVICE: | 2nd Stage Gas Compression Suction Drums
FLUID STATE: | VENT GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 796.4 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 18.1~ 22 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 18.1~ 22 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 47.7
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 22 ~ 59.88 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 18.08~ 1011 | - | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.013 ~0.98 | - | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | - | 94.65 | - | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 80 | CORROSION ALLOWANCE(mm) |  | 6 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting , Spring Return
|  |  | OUT | 2" | 80 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0160B-CN05-2"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Open
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/ Floating Type | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2" /300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Declutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | No
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | BZSC-2134B / BZSO-2134B
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | BSOV-2134B , PSOV-2134B | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No |  |  |  |  | FIRE PROOF DESIGN | 91 | PASSIVE FIRE PROTECTION |  | No
| 47 | QUICK EXHUST |  |  |  | Yes | [5 empty] | 92 | API 6FA REQUIREMENTS |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | SIL 3 REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | No | [5 empty] | 94 | PARTIAL STROKING VALVE TEST |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## BDV-2134C
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
Blow Down Valve
TAG NO: |  | BDV-2134C |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0009-D08 (3/3) | [6 empty] | SERVICE: | 2nd Stage Gas Compression Suction Drums
FLUID STATE: | VENT GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 796.4 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 18.1~ 22 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 18.1~ 22 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 47.7
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 22 ~ 59.88 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 18.08~ 1011 | - | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.013 ~0.98 | - | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | - | 94.65 | - | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 80 | CORROSION ALLOWANCE(mm) |  | 6 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting , Spring Return
|  |  | OUT | 2" | 80 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0160C-CN05-2"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Open
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/ Floating Type | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A216 Gr. WCB | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2" /300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Declutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | No
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | BZSC-2134C / BZSO-2134C
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | BSOV-2134C , PSOV-2134C | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No |  |  |  |  | FIRE PROOF DESIGN | 91 | PASSIVE FIRE PROTECTION |  | No
| 47 | QUICK EXHUST |  |  |  | Yes | [5 empty] | 92 | API 6FA REQUIREMENTS |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | SIL 3 REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | No | [5 empty] | 94 | PARTIAL STROKING VALVE TEST |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## BDV-2132A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
Blow Down Valve
TAG NO: |  | BDV-2132A |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0011-D09 (1/3) | [6 empty] | SERVICE: | 2nd Stage Gas Compression Air Coolers
FLUID STATE: | VENT GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 1414 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 54.1 ~ 62 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 54.1 ~ 62 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 62.4
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 22 ~ 60 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 59.63~ 1012 | - | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.014 ~ 0.976 | - | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | - | 94.65 | - | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 1 1/2" | 40S | CORROSION ALLOWANCE(mm) |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting , Spring Return
|  |  | OUT | 1 1/2" | 40S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0054A-FS00-1 1/2"-IS | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Open
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/ Floating Type | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 1 1/2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later |  | ` |  |  |  | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 1 1/2" /600# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 1 1/2" /600# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Declutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | No
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | BZSC-2132A / BZSO-2132A
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | BSOV-2132A , PSOV-2132A | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No |  |  |  |  | FIRE PROOF DESIGN | 91 | PASSIVE FIRE PROTECTION |  | No
| 47 | QUICK EXHUST |  |  |  | Yes | [5 empty] | 92 | API 6FA REQUIREMENTS |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | SIL 3 REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | No | [5 empty] | 94 | PARTIAL STROKING VALVE TEST |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## BDV-2132B
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
Blow Down Valve
TAG NO: |  | BDV-2132B |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0011-D09 (2/3) | [6 empty] | SERVICE: | 2nd Stage Gas Compression Air Coolers
FLUID STATE: | VENT GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 1414 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 54.1 ~ 62 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 54.1 ~ 62 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 62.4
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 22 ~ 60 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 59.63~ 1012 | - | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.014 ~ 0.976 | - | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | - | 94.65 | - | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 1 1/2" | 40S | CORROSION ALLOWANCE(mm) |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting , Spring Return
|  |  | OUT | 1 1/2" | 40S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0054B-FS00-1 1/2"-IS | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Open
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/ Floating Type | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 1 1/2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 1 1/2" /600# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 1 1/2" /600# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Declutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | No
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | BZSC-2132B / BZSO-2132B
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | BSOV-2132B , PSOV-2132B | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No |  |  |  |  | FIRE PROOF DESIGN | 91 | PASSIVE FIRE PROTECTION |  | No
| 47 | QUICK EXHUST |  |  |  | Yes | [5 empty] | 92 | API 6FA REQUIREMENTS |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | SIL 3 REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | No | [5 empty] | 94 | PARTIAL STROKING VALVE TEST |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## BDV-2132C
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
Blow Down Valve
TAG NO: |  | BDV-2132C |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0011-D09 (3/3) | [6 empty] | SERVICE: | 2nd Stage Gas Compression Air Coolers
FLUID STATE: | VENT GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 1414 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 54.1 ~ 62 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 54.1 ~ 62 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 62.4
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 22 ~ 60 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 59.63~ 1012 | - | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.014 ~ 0.976 | - | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | - | 94.65 | - | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 1 1/2" | 40S | إ |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting , Spring Return
|  |  | OUT | 1 1/2" | 40S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0054C-FS00-1 1/2"-IS | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Open
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/ Floating Type | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 1 1/2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 1 1/2" /600# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 1 1/2" /600# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Declutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | No
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | BZSC-2132C / BZSO-2132C
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | BSOV-2132C , PSOV-2132C | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No |  |  |  |  | FIRE PROOF DESIGN | 91 | PASSIVE FIRE PROTECTION |  | No
| 47 | QUICK EXHUST |  |  |  | Yes | [5 empty] | 92 | API 6FA REQUIREMENTS |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | SIL 3 REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | No | [5 empty] | 94 | PARTIAL STROKING VALVE TEST |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## BDV-2141
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
Blow Down Valve
TAG NO: |  | BDV-2141 |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0012-D08 | [6 empty] | SERVICE: | 2nd Stage Gas Compression Discharge Drum
FLUID STATE: | FLARE GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  |  | 1825 |  | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 53.9 ~ 62 | 53.9 ~ 62 | 53.9 ~ 62 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 53.9 ~ 62 | 53.9 ~ 62 | 53.9 ~ 62 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 90
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | 21 ~ 59.89 | 21 ~ 59.89 | 21 ~ 59.89 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 59.17 ~ 1012 | 59.17 ~ 1012 | 59.17 ~ 1012 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.014 ~ 0.976 | 0.014 ~ 0.976 | 0.014 ~ 0.976 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 106 | 106 | 106 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 1 1/2" | 160 | CORROSION ALLOWANCE(mm) |  | 3 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting , Spring Return
|  |  | OUT | 1 1/2" | 160 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0065-FN05-1 1/2"-IS | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Open
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/ Floating Type | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 1 1/2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A216 Gr. WCB | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 1 1/2" /600# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 1 1/2" /600# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Declutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | No
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | BZSC-2141 / BZSO-2141
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | BSOV-2141 | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No |  |  |  |  | FIRE PROOF DESIGN | 91 | PASSIVE FIRE PROTECTION |  | No
| 47 | QUICK EXHUST |  |  |  | Yes | [5 empty] | 92 | API 6FA REQUIREMENTS |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | SIL 3 REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | No | [5 empty] | 94 | PARTIAL STROKING VALVE TEST |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## BDV-2151
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
Blow Down Valve
TAG NO: |  | BDV-2151 |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0013-D08 | [6 empty] | SERVICE: | Dehydration Package
FLUID STATE: | VENT GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 4843 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 52.9 ~ 62 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 52.9 ~ 62 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 90
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 22~ 59.4 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 58.06 ~ 1012 | - | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.013 ~ 0.964 | - | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | - | 105.9 | - | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 3" | 80 | CORROSION ALLOWANCE(mm) |  | 6 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting , Spring Return
|  |  | OUT | 3" | 80 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0071-FN05-3"-IS | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Open
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/ Floating Type | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 3" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A216 Gr. WCB | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 3" /600# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 3" /600# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Declutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | No
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | BZSC-2151 / BZSO-2151
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | BSOV-2151 | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No |  |  |  |  | FIRE PROOF DESIGN | 91 | PASSIVE FIRE PROTECTION |  | No
| 47 | QUICK EXHUST |  |  |  | Yes | [5 empty] | 92 | API 6FA REQUIREMENTS |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | SIL 3 REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | No | [5 empty] | 94 | PARTIAL STROKING VALVE TEST |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2112
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2112 |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0004-D09 (2/2) | [6 empty] | SERVICE: | Slug Catcher System
FLUID STATE: | SLUG |  |  | PHASE: |  | LIQUID | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | Kg/H |  | 7873.8 | 7158 | 2505.3 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 18.5 | 18.5 | 18.5 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 18.5 | 18.5 | 18.5 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 47.7
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | 15.2~ 32.0 | 15.2~ 32.0 | 15.2~ 32.0 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 715 | 715 | 715 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.58 | 0.58 | 0.58 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | 6.487 | 6.487 | 6.487 | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 78 | 78 | 78 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 4" | 40 | CORROSION ALLOWANCE(mm) |  | 6 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 4" | 40 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | CDH-112-118-CN07-4"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 4" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A216 Gr. WCB | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 4"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 4"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2112 / XZSO-2112
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | ESOV-2112 | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes
| 49 | FILTER REGULATOR |  |  |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2121A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2121A |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0006-D09 (1/3) | [6 empty] | SERVICE: | 1st Stage Gas Compression Suction Drums
FLUID STATE: | PROCESS GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | 9530.4 | 8664 | 3032.4 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 5.1 | 5.1 | 5.1 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 5.1 | 5.1 | 5.1 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 18.2
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | 19.02~ 36.92 | 19.02~ 36.92 | 19.02~ 36.92 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 5.56 ~ 5.96 | 5.56 ~ 5.96 | 5.56 ~ 5.96 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.011 | 0.011 | 0.011 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 94.65 | 94.65 | 94.65 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 8" | 60 | CORROSION ALLOWANCE(mm) |  | 6 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 8" | 60 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0026A-AN07-8"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 8" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A216 Gr. WCB | [5 empty] | 60 | TRAVELING TIME |  | 9 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 8"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 8"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2121A / XZSO-2121A
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2121A , ESOV-2121A | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2121B
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2121B |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0006-D09 (2/3) | [6 empty] | SERVICE: | 1st Stage Gas Compression Suction Drums
FLUID STATE: | PROCESS GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | 9530.4 | 8664 | 3032.4 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 5.1 | 5.1 | 5.1 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 5.1 | 5.1 | 5.1 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 18.2
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | 19.02~ 36.92 | 19.02~ 36.92 | 19.02~ 36.92 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 5.56 ~ 5.96 | 5.56 ~ 5.96 | 5.56 ~ 5.96 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.011 | 0.011 | 0.011 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 94.65 | 94.65 | 94.65 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 8" | 60 | CORROSION ALLOWANCE(mm) |  | 6 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 8" | 60 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0026B-AN27-8"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 8" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A216 Gr. WCB | [5 empty] | 60 | TRAVELING TIME |  | 9 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 8"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 8"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2121B / XZSO-2121B
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2121B, ESOV-2121B | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2121C
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2121C |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0006-D09 (3/3) | [6 empty] | SERVICE: | 1st Stage Gas Compression Suction Drums
FLUID STATE: | PROCESS GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | 9530.4 | 8664 | 3032.4 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 5.1 | 5.1 | 5.1 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 5.1 | 5.1 | 5.1 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 18.2
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | 19.02~ 36.92 | 19.02~ 36.92 | 19.02~ 36.92 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 5.56 ~ 5.96 | 5.56 ~ 5.96 | 5.56 ~ 5.96 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.011 | 0.011 | 0.011 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 94.65 | 94.65 | 94.65 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 8" | 60 | CORROSION ALLOWANCE(mm) |  | 6 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 8" | 60 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0026C-AN07-8"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 8" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A216 Gr. WCB | [5 empty] | 60 | TRAVELING TIME |  | 9 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 8"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 8"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2121C / XZSO-2121C
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2121C, ESOV-2121C | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2122A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2122A |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0006-D09 (1/3) | [6 empty] | SERVICE: | 1st Stage Gas Compression Suction Drums
FLUID STATE: | CLOSED DRAIN |  |  | PHASE: |  | LIQUID | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 10000 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 4.9 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 4.9 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 13.9
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 36.78 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 998.5 | - | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.69 | - | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | 0.61 | 0.61 | 0.61 | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 221.3 | 221.3 | 221.3 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 10S | CORROSION ALLOWANCE(mm) |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 10S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | CDH-112-0021A-CS00-2"-NP | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2122A / XZSO-2122A
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2122A , ESOV-2122A | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2122B
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2122B |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0006-D09 (2/3) | [6 empty] | SERVICE: | 1st Stage Gas Compression Suction Drums
FLUID STATE: | CLOSED DRAIN |  |  | PHASE: |  | LIQUID | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 10000 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 4.9 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 4.9 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 13.9
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 36.78 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 998.5 | - | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.69 | - | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | 0.61 | 0.61 | 0.61 | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 221.3 | 221.3 | 221.3 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 10S | CORROSION ALLOWANCE(mm) |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 10S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | CDH-112-0021B-CS00-2"-NP | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2122B / XZSO-2122B
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2122B , ESOV-2122B | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2122C
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2122C |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0006-D09 (3/3) | [6 empty] | SERVICE: | 1st Stage Gas Compression Suction Drums
FLUID STATE: | CLOSED DRAIN |  |  | PHASE: |  | LIQUID | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 10000 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 4.9 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 4.9 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 13.9
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 36.78 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 998.5 | - | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.69 | - | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | 0.61 | 0.61 | 0.61 | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 221.3 | 221.3 | 221.3 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 10S | CORROSION ALLOWANCE(mm) |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 10S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | CDH-112-0021C-CS00-2"-NP | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2122C / XZSO-2122C
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2122C , ESOV-2122C | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2123A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2123A |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0006-D09 (1/3) | [6 empty] | SERVICE: | 1st Stage Gas Compression Suction Drums
FLUID STATE: | Process Gas |  |  | PHASE: |  | Gas | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | 9530.4 | 8664 | 3032.4 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 5.1 | 5.1 | 5.1 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 5.1 | 5.1 | 5.1 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 18.2
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | 19.02~ 36.92 | 19.02~ 36.92 | 19.02~ 36.92 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 5.56 ~ 5.96 | 5.56 ~ 5.96 | 5.56 ~ 5.96 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.011 | 0.011 | 0.011 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 94.65 | 94.65 | 94.65 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 160 | CORROSION ALLOWANCE(mm) |  | 6 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 160 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0024A-AN07-2"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2123A / XZSO-2123A
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2123A , ESOV-2123A | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2123B
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2123B |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0006-D09 (2/3) | [6 empty] | SERVICE: | 1st Stage Gas Compression Suction Drums
FLUID STATE: | Process Gas |  |  | PHASE: |  | Gas | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | 9530.4 | 8664 | 3032.4 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 5.1 | 5.1 | 5.1 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 5.1 | 5.1 | 5.1 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 18.2
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | 19.02~ 36.92 | 19.02~ 36.92 | 19.02~ 36.92 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 5.56 ~ 5.96 | 5.56 ~ 5.96 | 5.56 ~ 5.96 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.011 | 0.011 | 0.011 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 94.65 | 94.65 | 94.65 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 160 | CORROSION ALLOWANCE(mm) |  | 6 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 160 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0024B-AN07-2"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2123B / XZSO-2123B
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2123B , ESOV-2123B | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2123C
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2123C |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0006-D09 (3/3) | [6 empty] | SERVICE: | 1st Stage Gas Compression Suction Drums
FLUID STATE: | Process Gas |  |  | PHASE: |  | Gas | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | 9530.4 | 8664 | 3032.4 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 5.1 | 5.1 | 5.1 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 5.1 | 5.1 | 5.1 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 18.2
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | 19.02~ 36.92 | 19.02~ 36.92 | 19.02~ 36.92 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 5.56 ~ 5.96 | 5.56 ~ 5.96 | 5.56 ~ 5.96 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.011 | 0.011 | 0.011 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 94.65 | 94.65 | 94.65 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 160 | CORROSION ALLOWANCE(mm) |  | 6 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 160 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0024C-AN07-2"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2123C / XZSO-2123C
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2123C , ESOV-2123C | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2124A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2124A |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0006-D09 (1/3) | [6 empty] | SERVICE: | 1st Stage Gas Compression Suction Drums
FLUID STATE: | Gas |  |  | PHASE: |  | Nitrogen | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 25 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 7.5 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 7.5 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 12.5
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 60 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 8.62 | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.019988 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | - | 33.94 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 40 | CORROSION ALLOWANCE(mm) |  | 1 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 40 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | NIT-112-0006A-AN01-2"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2124A / XZSO-2124A
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2124A , ESOV-2124A | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2124B
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2124B |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0006-D09 (2/3) | [6 empty] | SERVICE: | 1st Stage Gas Compression Suction Drums
FLUID STATE: | Gas |  |  | PHASE: |  | Nitrogen | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 25 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 7.5 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 7.5 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 12.5
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 60 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 8.62 | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.019988 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | - | 33.94 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 40 | CORROSION ALLOWANCE(mm) |  | 1 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 40 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | NIT-112-0006B-AN01-2"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2124B / XZSO-2124B
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2124B , ESOV-2124B | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2124C
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2124C |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0006-D09 (3/3) | [6 empty] | SERVICE: | 1st Stage Gas Compression Suction Drums
FLUID STATE: | Gas |  |  | PHASE: |  | Nitrogen | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 25 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 7.5 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 7.5 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 12.5
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 60 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 8.62 | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.019988 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | - | 33.94 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 40 | CORROSION ALLOWANCE(mm) |  | 1 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 40 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | NIT-112-0006C-AN01-2"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2124C / XZSO-2124C
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2124C , ESOV-2124C | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2131A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2131A |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0009-D08 (1 of 3) | [6 empty] | SERVICE: | 2nd Stage Gas Compression Suction Drums
FLUID STATE: | CLOSED DRAIN |  |  | PHASE: |  | LIQUID | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 10000 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 18.1 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 18.1 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 30.3
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 59.88 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 981.1 | - | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.496 | - | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | 3.23 | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 221.5 | 221.5 | 221.5 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 10S | CORROSION ALLOWANCE(mm) |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 10S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | CDH-111-0023A-CS00-2"-NP | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2131A / XZSO-2131A
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2131A , ESOV-2131A | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2131B
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2131B |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0009-D08 (2 of 3) | [6 empty] | SERVICE: | 2nd Stage Gas Compression Suction Drums
FLUID STATE: | CLOSED DRAIN |  |  | PHASE: |  | LIQUID | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 10000 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 18.1 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 18.1 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 30.3
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 59.88 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 981.1 | - | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.496 | - | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | 3.23 | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 221.5 | 221.5 | 221.5 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 10S | CORROSION ALLOWANCE(mm) |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 10S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | CDH-111-0023B-CS00-2"-NP | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2131B / XZSO-2131B
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2131B, ESOV-2131B | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2131C
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2131C |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0009-D08 (3 of 3) | [6 empty] | SERVICE: | 2nd Stage Gas Compression Suction Drums
FLUID STATE: | CLOSED DRAIN |  |  | PHASE: |  | LIQUID | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 10000 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 18.1 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 18.1 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 30.3
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 59.88 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 981.1 | - | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.496 | - | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | 3.23 | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 221.5 | 221.5 | 221.5 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 10S | CORROSION ALLOWANCE(mm) |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 10S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | CDH-111-0023C-CS00-2"-NP | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2"/300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2131C / XZSO-2131C
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2131C, ESOV-2131C | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2133A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2133A |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0011-D09 (1 of 3) | [6 empty] | SERVICE: | 2nd Stage Gas Compression Air Coolers
FLUID STATE: | PROCESS GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | 9530.4 | 8664 | 3032.4 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 54.1 | 54.1 | 54.1 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 54.1 | 54.1 | 54.1 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 62.4
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 60 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 49.41 ~ 59.63 | 49.41 ~ 59.63 | 49.41 ~ 59.63 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.014 | 0.014 | 0.014 | - | 0.013909
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 94.66 | 94.66 | 94.66 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 6" | 40S | CORROSION ALLOWANCE(mm) |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 6" | 40S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0055A-FS00-6"-IS | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 6" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 7 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 6"/600# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 6"/600# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2133A / XZSO-2133A
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2133A, ESOV-2133A | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2133B
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2133B |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0011-D09 (2 of 3) | [6 empty] | SERVICE: | 2nd Stage Gas Compression Air Coolers
FLUID STATE: | PROCESS GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | 9530.4 | 8664 | 3032.4 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 54.1 | 54.1 | 54.1 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 54.1 | 54.1 | 54.1 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 62.4
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 60 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 49.41 ~ 59.63 | 49.41 ~ 59.63 | 49.41 ~ 59.63 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.014 | 0.014 | 0.014 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 94.66 | 94.66 | 94.66 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 6" | 40S | CORROSION ALLOWANCE(mm) |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 6" | 40S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0055B-FS00-6"-IS | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 6" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 7 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 6"/600# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 6"/600# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2133B / XZSO-2133B
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2133B, ESOV-2133B | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2133C
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2133C |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0011-D09 (3 of 3) | [6 empty] | SERVICE: | 2nd Stage Gas Compression Air Coolers
FLUID STATE: | PROCESS GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | 9530.4 | 8664 | 3032.4 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 54.1 | 54.1 | 54.1 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 54.1 | 54.1 | 54.1 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 62.4
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 60 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 49.41 ~ 59.63 | 49.41 ~ 59.63 | 49.41 ~ 59.63 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.014 | 0.014 | 0.014 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 94.66 | 94.66 | 94.66 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 6" | 40S | CORROSION ALLOWANCE(mm) |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 6" | 40S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0055C-FS00-6"-IS | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 6" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 7 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 6"/600# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 6"/600# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2133C / XZSO-2133C
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2133C, ESOV-2133C | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2134A
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2134A |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0011-D09 (1/3) | [6 empty] | SERVICE: | 2nd Stage Gas Compression Air Coolers
FLUID STATE: | Purge Gas |  |  | PHASE: |  | Gas | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 25 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 54.1 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 54.1 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 62
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 60 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 8.62 | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.019988 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | - |  | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 40S | CORROSION ALLOWANCE(mm) |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 40S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0030A-FS00-2"-NP | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2"/600# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/600# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2134A / XZSO-2134A
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2134A , ESOV-2134A | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2134B
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2134B |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0011-D09 (2/3) | [6 empty] | SERVICE: | 2nd Stage Gas Compression Air Coolers
FLUID STATE: | Purge Gas |  |  | PHASE: |  | Gas | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 25 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 54.1 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 54.1 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 62
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 60 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 8.62 | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.019988 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | - |  | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 40S | CORROSION ALLOWANCE(mm) |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 40S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0030B-FS00-2"-NP | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2"/600# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/600# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2134B / XZSO-2134B
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2134B , ESOV-2134B | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2134C
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2134C |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0011-D09 (3/3) | [6 empty] | SERVICE: | 2nd Stage Gas Compression Air Coolers
FLUID STATE: | Purge Gas |  |  | PHASE: |  | Gas | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 25 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 54.1 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 54.1 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 62
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 60 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 8.62 | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.019988 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | - |  | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 40S | CORROSION ALLOWANCE(mm) |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 40S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0030C-FS00-2"-NP | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2"/600# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2"/600# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2134C / XZSO-2134C
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2134C , ESOV-2134C | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2142
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2142 |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0012-D08 | [6 empty] | SERVICE: | 2nd Stage Gas Compression Discharge Drum
FLUID STATE: | PROCESS GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | 18977.739 | 17252.49 | 6038.3715 | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 53.9 | 53.9 | 53.9 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 53.9 | 53.9 | 53.9 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 90
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | 59.89 | 59.89 | 59.89 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 49.41~ 59.17 | 49.41~ 59.17 | 49.41~ 59.17 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.014 | 0.014 | 0.014 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | 3.23 | 3.23 | 3.23 | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 106 | 106 | 106 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 6" | 80 | CORROSION ALLOWANCE(mm) |  | 3 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 6" | 80 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0067-FN05-6"-IS | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 6" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A216 Gr. WCB | [5 empty] | 60 | TRAVELING TIME |  | 7 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 6" /600# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 6" /600# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2142 / XZSO-2142
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2142, ESOV-2142 | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2143
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2143 |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0012-D08 | [6 empty] | SERVICE: | 2nd Stage Gas Compression Discharge Drum
FLUID STATE: | PROCESS GAS |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 1500 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | 53.9 | 53.9 | 53.9 | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | 53.9 | 53.9 | 53.9 | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 90
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | 59.89 | 59.89 | 59.89 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | 49.23~ 59.17 | 49.23~ 59.17 | 49.23~ 59.17 | -
| 7 | VISCOSITY | [8 empty] | CP |  | 0.014 | 0.014 | 0.014 | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 106 | 106 | 106 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 80 | CORROSION ALLOWANCE(mm) |  | 3 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 80 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | GAS-111-0061-FN05-2"-IS | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A216 Gr. WCB | [5 empty] | 60 | TRAVELING TIME |  | 7 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2" /600# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2" /600# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | YES | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2143 / XZSO-2143
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | ESOV-2143, PSOV-2143 | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | No | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUAL PNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2144
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2144 |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0012-D08 | [6 empty] | SERVICE: | 2nd Stage Gas Compression Discharge Drum
FLUID STATE: | CLOSED DRAIN |  |  | PHASE: |  | LIQUID | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 11500 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 53.9 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 53.9 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 62.4
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 59.9 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 830~ 982 | - | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.442~ 0.495 | - | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | 4.43 | 4.43 | 4.43 | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | 221.9 | 221.9 | 221.9 | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 40S | CORROSION ALLOWANCE(mm) |  | 0 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 40S | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | CDH-112-0025-FS00-2"-NP | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A351 GR.CF3M | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2" /600# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2" /600# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+RPTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2144 / XZSO-2144
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | RPTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2144, ESOV-2144 | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2271
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2271 |  | P&ID NO : |  | BK-GCS-PEDCO-120-PR-PI-0022-D08 | [6 empty] | SERVICE: | Fuel Gas System
FLUID STATE: | CLOSED DRAIN |  |  | PHASE: |  | LIQUID | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 603.15 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 4.9 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 4.9 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | - | - | 18.2
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | - | 18.88~ 36.7 | - | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 842~ 852 | - | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.6934 ~ 1.03 | - | -
| 8 | VAPOR PRESSURE Pv | [8 empty] | bar(a) |  | - | 0.448 | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | - | 221.3 | - | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 2" | 160 | CORROSION ALLOWANCE(mm) |  | 6 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 2" | 160 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | CDH-112-0004-AN07-2"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 2" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A216 Gr. WCB | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 2" /300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 2" /300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2271 / XZSO-2271
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2271, ESOV-2271 | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes |  |  |  |  | FIRE PROOF DESIGN | 92 | PASSIVE FIRE PROTECTION |  | No
| 49 | FILTER REGULATOR |  |  |  | Yes | [5 empty] | 93 | API 6FA REQUIREMENTS |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes | [5 empty] | 94 | SIL 3 REQUIREMENTS |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | Required | [5 empty] | 95 | PARTIAL STROKING VALVE TEST |  | Yes
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | Yes | [5 empty] | 96
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02

## XV-2301
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For ON/OFF & Shutdown Valves
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9038 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
On-Off Valve
TAG NO: |  | XV-2301 |  | P&ID NO : |  | BK-GCS-PEDCO-120-SA-PI-0001-D05 (1/8) | [6 empty] | SERVICE: | Fire Water System
FLUID STATE: | FIRE WATER |  |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone2, IIB, T4
SERVICE CONDITION | ITEM | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [8 empty] | kg/h |  | - | 29910 | - | -
| 2 | INLET PRESSURE | [8 empty] | bar(g) |  | - | 1 | - | -
| 3 | OUTLET PRESSURE | [8 empty] | bar(g) |  | - | 0.95 | - | -
| 4 | DIFFERENTIAL PRESSURE | [8 empty] | bar(g) |  | - | 0.05 | - | -
| 5 | INLET TEMPERATURE | [8 empty] | °C |  | 55 | AMB | 5 | -
| 6 | DENSITY | [8 empty] | kg/m3 |  | - | 997 | - | -
| 7 | VISCOSITY | [8 empty] | CP |  | - | 0.81 | - | -
| 8 | VAPOR PRESSURE Pv | [10 empty] | - | - | - | -
| 9 | CRITICAL PRESSURE | [8 empty] | bar(a) |  | - | - | - | -
LINE | 10 | PIPE LINE SIZE & SCHEDULE | IN | 3" | 40 | CORROSION ALLOWANCE(mm) |  | 3 |  |  | ACTUATOR | 53 | TYPE |  | Single Acting, Spring Return
|  |  | OUT | 3" | 40 | [6 empty] | 54 | SIZE |  | VTA
| 11 | LINE NO. | FWA-112-0007-AN04-3"-PT | [8 empty] | 55 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 56 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  |  | 3" | [5 empty] | 57 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP. |  |  |  | As per PMS | [5 empty] | 58 | AVAILABLE AIR SUPPLY PRESSURE |  | MAX/NOR/MIN: 10/7/3 bar-g
| 15 | MFR. & MODEL |  |  |  | Will be finalized later | [5 empty] | 59 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  |  | ASTM A216 Gr. WCB | [5 empty] | 60 | TRAVELING TIME |  | 5 S
| 17 | LINER MATERIAL / ID |  |  |  | VTA | [5 empty] | 61 | FUNCTION |  | On/Off
| 18 | END CONNECTION | IN |  |  | 3" /300# | [5 empty] | 62 | LOCAL POSITION INDICATOR |  | Required
|  |  | OUT |  |  | 3" /300# | [5 empty] | 63 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  |  | RF | [5 empty] | 64 | HAND WHEEL TYPE |  | Clutchable side mounted
| 20 | END EXT./MATL. |  |  |  | N/A | [5 empty] | 65 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  |  | (Note 18 in Page 4) | [5 empty] | 66 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  |  | Standard | [5 empty] | 67 | MFR. & MODEL |  | Will be finalized later
| 23 | LUBE & ISO VALVE |  |  |  | No |  |  |  |  | POSITIONER | 68 | TYPE |  | N/A
| 24 | PACKING MATERIAL |  | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 69 | MFR. & MODEL |  | Will be finalized later
| 25 | ENTRY DESIGN |  |  |  | Top Entry | [5 empty] | 70 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  |  | No | [5 empty] | 71 | GAUGES |  | N/A
TRIM | 27 | TRIM | TYPE | MATERIAL |  | VTA |  |  | 316 SS+PTFE |  |  | 72 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  |  | VTA |  |  | VTA |  |  | 73 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 74 | TAG NO. : |  | XZSC-2301 / XZSO-2301
| 30 | BALANCED / UNBALANCED |  |  |  | BALANCED | [5 empty] | 75 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT |  | VTA | VTA | VTA |  |  |  | 76 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  |  | 316 SS | [5 empty] | 77 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT | TYPE | MATERIAL |  | Soft Seat |  |  | PTFE |  |  | 78 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  |  | VTA | [5 empty] | 79 | WEATHER PROTECTION |  | IP-65
| 35 | STEM | TYPE | MATERIAL |  | Anti-Blow Out |  |  | 316 SS |  |  | 80 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d" ,IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  |  | ANSI Class VI | [5 empty] | 81 | MFR. & MODEL |  | Will be finalized later
| 37 | VALVE STEM EXTENSION REQUIREMENT |  |  |  | YES |  |  |  |  | AIR SET | 82 | SET PRESSURE |  | Yes
SOLENOID VALVE | 38 | TAG NO |  |  |  | PSOV-2301 | [5 empty] | 83 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  |  | 3 Way | [5 empty] | 84 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL |  | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 85 | MFR. & MODEL |  | Will be finalized later
| 41 | ELE. CERTIFICATE |  | ELE. CONNECTION |  | EEx "d" ,IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 86 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  |  | Yes | [5 empty] | 87 | HYDRO PRESSURE |  | Required
| 43 | Power Supply |  |  |  | 24 VDC | [5 empty] | 88 | FUNCTIONAL TEST |  | Required
| 44 | Pnu. Connection |  |  |  | 1/4" NPT | [5 empty] | 89
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  |  | No | [5 empty] | 90
| 46 | BLOCK RELAY |  |  |  | No | [5 empty] | 91
| 47 | QUICK EXHUST |  |  |  | Yes
| 49 | FILTER REGULATOR |  |  |  | Yes
| 50 | VOLUME TANK |  |  |  | Yes
| 51 | MECHANICAL POSITION INDICATOR |  |  |  | No
| 52 | MANUALPNEUMATIC BYPASS VALVE FOR SOLENOID VALVE |  |  |  | No
NOTE: | VTA : VENDOR TO ADVISE AT BIDDING STAGE |  |  |  |  | VTC: VENDOR TO CONIFRM
(1) PMS: Piping material specification. (2) All material shall be suitable for minimum design metal temperature. (3) Shall be stated by vendor at quotation stage. (4) Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
D02