| Row | Clarification Title | Bidder reply (1st round) | Conclusion (2nd round) | Bidder reply (2nd round) | Conclusion (final/TCM) |
| --- | --- | --- | --- | --- | --- |
| GENERAL |  |  |  |  |  |
|  | Vendor to confirm that in case of contradiction between this TCL and offer; vendor confirmation of compliance through this technical clarification is governed and shall be followed by vendor after order. In such case offer won’t be considered as basis of any claim after order. | Noted. |  |  |  |
|  | Bidder shall confirm his full compliance to meet all purchaser documents listed and attached to MR, code / standards listed in MR with ref. No. “BK-GCS-PEDCO-120-ME-MR-0009 “as well as MR requirements. All deviations shall be listed in project deviation form, attach to this TCL, signed and stamped. Notes: 1-Any exception and deviation from the requirements of MR and the related specifications including referenced codes & standards shall be clearly declared by vendor in writing for purchaser’s approval at bid stage by using of the format included in “Letter Of Conformity” attached to material requisition. Raising no deviation to any single requirement means full compliance of vendor quotation to that requirement. Purchaser has no responsibility to discover deviations or alternatives scattered over the proposal in addition to what proclaimed explicitly in deviation list; hence such deviation (if any) is disregarded and shall not be considered for vendor claim in future. (Vendor to confirm) 2- Bidder shall confirm that all MR attachments listed in MR are available for her for review at bid stage. 3-Considering items 1 & 2, please note that any deviation at detail stage will not be accepted by purchaser. 4- MR scope of work and supply shall be signed and stamped by vendor. | Noted. |  |  |  |
|  | Bidder shall provide following documents while bidding: 1- Copy of valid quality system certificate(ISO 9001/2 or 3) 2- Sub- vendors / sub-suppliers list. 3- Deviation list with letter of conformity (Refer to item A2 above) 4- Reference and Experience List 5- Joint venture agreement (If any) with any company to design / fabrication of equipment. In case of joint venture ; qualified documents of the company who is part of joint venture shall be also submitted | Please find the attachment. |  |  |  |
|  | Bidder shall submit selected Sub-Vendor List based on Project AVL, before proceeding with any purchasing activity. Vendors shall be selected from A.V.L Based On Products. Please confirm. | Confirm. Please specify the project AVL. |  |  |  |
|  | Bidder to confirm that surface preparation and painting of all equipment material including valves , pipes , fittings and everything within the package are in accordance with project painting specification with ref. "BK-GNRAL-PEDCO-000-PI-SP-0006" attached to MR. | Confirm. |  |  |  |
|  | Bidder to confirm that Packing, Marking, transporting procedure (BK-GNRAL-PEDCO-000-QC-PR-0045) for Shipment will be done in accordance to the project specification attached to the MR. | Confirm. |  |  |  |
|  | Inspection and Test Plan / Quality Control Plan and their related inspection level (Witness, Hold, Review and Approval) shall be at least in accordance with MR and all project requirement such as NDT PROCEDURE. Any deviation is not accepted unless otherwise specified in deviation list and approved by Purchaser. | Please refer to sample ITP. ITP will be finalized during PIM. |  |  |  |
|  | Bidder to confirm that for all pressure parts and those required special consideration or stainless steel as well as for supports the material certificate should be in accordance with EN 10204, 3.1 Material certificate for non-pressure parts shall be in accordance with EN 10204,3.1 or 2.2 | Confirm |  |  |  |
|  | Bidder to confirm that all native files due to all calculations and drawings shall be submitted for purchaser approval after order. |  |  |  |  |
|  | Following documents shall be submitted at bid stage (as a minimum requirement): 1. Vendor Catalogue 2. Quality Assurance Manual /Quality Management System Certificate (according to latest rev. of ISO) 3. P&IDs 4. Manufacturing Master Time Schedule Per Equipment (Including Design, Procurement, Fabrication, Test, Packing, Delivery) 5-Sectional drawing with BOM shall be submitted by vendor. 6-Noise Data 7-GA DWG with outline dimension, weights, suction and discharge nozzle load table and etc. shall be submitted by vendor in next revision. GAD shall include the arrangement of Pumps & their drivers and all auxiliaries. (driver, coupling, seal plan, cooling system (if any) and lubrication system (if any) 8. Utility Consumption List | Please refer to attachment. |  |  |  |
|  | Bidder shall confirm the scope of work and supply are fully in accordance with MR and its attachment with following items: 1- The consequences of HAZOP and SIL study shall be in vendor scope of supply and work. 2- Participation in technical meeting whenever it is necessary by Purchaser/Client to close engineering document after order is in vendor scope 3- Lifting lugs for erection with sling shackle and etc. shall be designed and supplied by vendor 4-N2 preservation with pressure regulator, valve & flexible hoses during transportation & 18 months of site storage based on requirements in MR shall be in vendor scope of supply / work. 5- All utility conditions shall be as per document "Process basis of Design Document; Doc. No: BK-GNRAL-PEDCO-000-PR-DB-0001 ". Moreover, bidder shall consider utility noted condition as per project design data. If other utility condition is needed, whole required facilities is in vendor scope of work/supply. 6- Anchor bolts | - If applicable - Noted. - Noted. - Noted. - Noted. |  |  |  |
|  | Vendor shall confirm Pumps and Equipment’s are fully suitable for outdoor installation/operation under project site conditions “Process Basis of Design; BK-GNRAL-PEDCO-000-PR-DB-0001 “without requiring any additional protection. | Noted, |  |  |  |
|  | Vendor shall send references list for each pump category with the following information: - Specified pumps models - Range of temperature - Capacity of the pumps - Differential head | Please refer to attachment. |  |  |  |
|  | Pre-commissioning, commissioning and start up spare parts shall be supplied by vendor. Vendor shall confirm to provide all required spare parts as per project spare part list attached to MR. | Noted. |  |  |  |
|  | Following items shall be considered (supplied) and included in the bid documentation: • Spare parts for commissioning and start-up • Spare parts for two years operation; a qualified and complete list based on E&C-QC-SP-1 • Capital spare parts (as option / if any) | Noted. |  |  |  |
|  | List of special tools required for the quoted pumps. Necessary special tools for erection/ installation and maintenance, if any, shall be included in supply. | Please refer to attachment. |  |  |  |
|  | Vendor shall warranty the engineering, materials and workmanship of the equipment/goods. Under this warranty, all materials, parts, and assemblies found to be defective during the guarantee period shall be replaced free of charge by VENDOR. | Noted. |  |  |  |
|  | The guarantee period shall be eighteen (18) months from the date of delivery or twelve (12) months from the date of mechanical completion & start-up, whichever occurs later. Also bidder to confirm performance guarantee requirements based on relevant data sheets & specifications (attached to the equipment PMR). | Noted. |  |  |  |
| PROCESS |  |  |  |  |  |
|  | All Equipment shall be designed as per project design criteria | Noted. |  |  |  |
| MECHANIC |  |  |  |  |  |
|  | The manufacturer should fill all the datasheets of the pumps with doc No: BK-GCS-PEDCO-120-ME-DT-0024 BK-GCS-PEDCO-120-ME-DT-0022 BK-GCS-PEDCO-120-ME-DT-0019 | Noted, |  |  |  |
|  | Design and supply of all interconnecting piping between equipment and all instruments, valves and … on them is in the vendor's scope. Also all between skid piping (including supporting) c/w all instrument and valve on them shall be designed, prefabricated and supplied by vendor. Detailed isometric DWGs shall be submitted for them. Note1: On skid piping to be assembled at vendor's shop. Note2; outside skid piping to be prefabricated and match marked for site assembling. | Just at skid is confirm. |  |  |  |
|  | ASTM number and grade of all supplied material to be specified. | Noted. |  |  |  |
|  | Design and supply of heat tracing c/w supports, clips, and other provisions (including panels, heating cables and relevant connectors, electrical cables, junction boxes and thermostats) shall be part of the vendor scope. | Is not required. |  |  |  |
|  | The coupling shall be of the API671 forged-steel, non-lubricated, flexible-element spacer type. The flexible elements shall be stainless steel metallic disk. |  |  |  |  |
|  | Vendor shall specify the coupling balancing grade and balancing method as per API671. | Noted |  |  |  |
|  | Positive material identification (PMI), pickling and passivation for non-carbon steel material to be included in vendor’s scope of work. |  |  |  |  |
|  | All vents and drains of the package to be valved, manifolded and to be routed to the edge of skid. | Noted. |  |  |  |
|  | Test procedures shall be Submitted by vendor based on project´s document | Noted. |  |  |  |
|  | Couplings shall be of two-piece, flexible, spacer type, permitting change of flexible membrane without disturbing the alignment of shafts. |  |  |  |  |
|  | The coupling guard shall be of non-sparking material. | Noted. |  |  |  |
|  | Design code for Centrifugal API pumps, and sealing system shall be API 610 11th Ed,IPS-G-PM-105. and API 682 4th Ed, respectively (w/considering relevant project specifications for centrifugal pump for Process Services “Doc. No. BK-GCS-PEDCO-120-ME-SP-0003" | Noted. |  |  |  |
|  | Seal data sheet (based on API 682 4th Ed.) shall be provided by vendor after order to be approved by Purchaser. | After order is confirmed. |  |  |  |
|  | All flange connection at battery limit shall be according to ASME B16.5, please confirm. | Noted. |  |  |  |
|  | 4 hour mechanical running test after oil stabilization is required | Noted. |  |  |  |
|  | The stabilized bearing-housing temperature shall not exceed 82 °C (180 °F) when operating at an ambient temperature | Noted. |  |  |  |
|  | Derating factor (max. Ambient temperature 50 ºC & Altitude: 12.5 m) shall be considered for motor sizing. The derating factor to be specified in the quotation. | The motor sizing is at site condition. |  |  |  |
|  | For recommended models, the impeller diameter shall not be more than 90% of the maximum Size which can be accommodated in the casing. | Noted. |  |  |  |
|  | Allowable nozzle forces and moments should comply API 610 11th Ed. | Noted. |  |  |  |
|  | Bidder to consider the stainless steel name plate (including information as per PURCHASER advices) for the equipment. | Noted. |  |  |  |
|  | Please specify overhead clearance (maintenance area) on pumps outline drawing. | Noted. |  |  |  |
|  | Please indicate the pump rotation direction on GAD | Noted. |  |  |  |
|  | Attached TBE form (Attachment#1) to be filled and sent via next response on TCL. | Noted. |  |  |  |
| PIPING & MATERIAL |  |  |  |  |  |
|  | Please send us General Arrangement Drawing of Pumps | Please refer to sample GA. |  |  |  |
|  | Catalogue for equipment shall be issued by vendor. | Noted. |  |  |  |
| SAFETY |  |  |  |  |  |
|  | Vendor confirms that the Noise level @ 1m will not exceed 85 dB | Confirm. Is <85 |  |  |  |
| ELECTRICAL |  |  |  |  |  |
|  | All electrical equipment shall comply with electrical references & standard that mentioned on material requisition. IPS-E-EL-100 (1), IPS-M-EL-131 (2). | Noted. |  |  |  |
|  | All Electrical equipment shall be suitable for environmental data based on process design criteria. | Noted. |  |  |  |
|  | All documents related to electro motor shall be submitted by vendor such as, motor data sheet, motor outline drawing & etc. | After order. |  |  |  |
|  | Vendor list & sub vendor list of manufacture shall be according to project AVL. | Confirm.Please specify the project AVL. |  |  |  |
|  | A complete set of spare parts for commissioning shall be supplied for each motor. | According to Table 2-11. LOW VOLTAGE ELECTRIC MOTORS, the commissioning spare part is note required. Please clarify. |  |  |  |
|  | The equipment shall be factory tested. Certified copies of test reports shall be submitted to the purchaser. | Noted. |  |  |  |
|  | Data sheet & Specification of LV induction motor have been attached to MR. Please follow them. | Noted, Motor datasheet will be filled by motor manufacture after order. |  |  |  |
|  | Data sheet for LV induction motor shall be filled and submitted. | After order. |  |  |  |
|  | Principle of motor sizing shall be specified for all motors. |  |  |  |  |
|  | For LV (400V) electric motors internal & external earth lugs shall be considered | Noted. |  |  |  |
|  | Motor painting color shall be RAL 7032. | Noted. |  |  |  |
|  | Low Voltage Electric motors (P<=150kW) shall be suitable for 400V±5% and 50Hz±2% , windings shall be delta connected and motor shall be suitable for DOL starting method. | Noted. |  |  |  |
|  | Starting current with positive tolerances shall not exceed from specified values in below (related to motor rated current): 750% for motors with rated power P<=75kW 650% for motors with rated power 75<P<=150kW |  |  |  |  |
|  | Motors shall be capable to starting their load with 80% of voltage at its terminals |  |  |  |  |
|  | Since power rated of motor will be finalized later, therefore size of cable & gland will be submitted after PO. Vendor shall follow the requirement. | Noted. |  |  |  |
|  | Inspection/test of motors shall be according to MR. | Please refer to sample ITP. |  |  |  |
|  | Motor bearings, fan & space heater shall be Considered in two years spare part list. | Noted. Space heater is not required. |  |  |  |
|  | For outdoor motors, sun/rain protection canopy shall be considered by vendor. | Confirm |  |  |  |
|  | Please clarify for items in MRQ, electrical heat tracing is required or not? If heat tracing required, providing materials (heater cable, thermostat box, electric panel etc) and design (isometric drawings, calculation, bill of material) will be in vendor scope of work/supply. | Not required. |  |  |  |
| STRUCTURE |  |  |  |  |  |
|  | The exact dimensions and size of the skid and the proper alignment under the skid shall be determined. | It will be submitted at GA. |  |  |  |
|  | Based on STD2800 this site is located at High Risk Area which is named Seismic Zone 2. also according to ASCE 7 (2010) Seismic Zone is equal to Zone 3 with Seismic Importance Factor 1.25 |  |  |  |  |
|  | According to project spec. mean hourly with 50Yr return period speed shall be considered 120 Km/hr. |  |  |  |  |
|  | The type and location of the anchor bolt should be provided by vendor. This item shall be considered in G.A. Drawings. | It will be submitted at GA. |  |  |  |
|  | The static and dynamic loads of the equipment shall be presented at the foundation level. The elevation and location of the equipment center of mass shall be determined. | After P.O. |  |  |  |
|  | The following codes & standards should be considered in the civil & structure section: AWS , ASCE7-10 , INBC6 |  |  |  |  |
| QC |  |  |  |  |  |
|  | Vendor shall sign and stamp all engineering documents which are attached to PMR without Deviation. | Noted. |  |  |  |
|  | Vendor shall confirm and guarantee suitability of selected materials of each pump parts according to material class for pump service. | Confirm. |  |  |  |
|  | Vendor shall confirm to supply raw materials from approved vendor list and submit all required material certificates for TPI approval before manufacturing. | Material certificate will be submitted for main parts. |  |  |  |
|  | Vendor shall confirm to issue and take client approval for vendor documents as per VPIS before any raw material supply or manufacturing. | Noted. |  |  |  |
|  | Vendor shall confirm material selection for each part of package is suitable for service condition and design life. | Noted. |  |  |  |
|  | Welding book (including WPS, PQR, weld map and NDT map) shall be prepared by vendor and submitted for purchaser approval (pressure parts, and structural). No welding shall be commenced before receiving approved welding book. | Noted. |  |  |  |
|  | Vendor to confirm, the package shall be designed and constructed so that requires minimum site work (preparation and welding) while fulfills transportation limits. | Confirm. Please refer to QC plan. |  |  |  |
|  | Vendor shall confirm to have full responsibility on quality control of manufactured equipment and shall be responsible for any deviations or non-conformities before, during and after manufacturing and after installation and start up. | Noted. |  |  |  |
|  | Vendor shall confirm to employ certified and expert workers and inspectors and to use calibrated measuring instruments according to regulations of ISO 3834 and ISO 9001. | ISO 9001 is confirm. |  |  |  |
|  | Vendor shall confirm to perform and report all required inspection and tests according to project specification and datasheets and reference standards and approved ITP including visual, dimensional, NDT, PMI, PWHT, Hardness, Hydrotest, Performance, Running, … | Please refer to sample ITP. |  |  |  |
|  | Vendor shall confirm to observe health & safety precautions and regulations during manufacturing for workers, inspectors, engineers and visitors. Vendor shall confirm observe environmental regulations during manufacturing processes such as casting, machining, welding, etc. | Confirm. |  |  |  |
|  | Vendor to confirm to prepare final data book according to project FDB requirements. | Confirm |  |  |  |