## COVER
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE FOR CENTRIFUGAL PUMPS FOR GENERAL SERVICES
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از5
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | ME | TB | 0010 | D00
طرح نگهداشت و افزایش تولید 27 مخزن
TBE FOR CENTRIFUGAL PUMPS FOR GENERAL SERVICES نگهداشت و افزایش تولید میدان نفتی بینک
D00 |  | AUG.2024 |  | IFI |  |  |  | V.Amjadi |  |  | M.Fakharian |  | M.Sadeghian
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 3 |  |  |  | CLIENT Doc. Number: F0Z-709234
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE FOR CENTRIFUGAL PUMPS FOR GENERAL SERVICES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از5
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | ME | TB | 0010 |  | D00
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | [7 empty] | 65
2 | X | [7 empty] | 66
3 | X | [7 empty] | 67
4 | X | [7 empty] | 68
5 | X | [7 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## PUMPS for General Services
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE FOR CENTRIFUGAL PUMPS FOR GENERAL SERVICES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه |  | شماره صفحه: 3 از 5
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | ME | TB |  | 0010 | D00
REQ. NO. |  | BK-GCS-PEDCO-120-ME-MR-0010 |  | BIDDER NAME: |  |  | ARYA SEPEHR KEYHAN (ASK) |  | BERKEH |  |  | NAVID SAHAND |  | PETRO RAHAN
QUOTATION NO.: | [6 empty] | 1405-0010-1548-205A0 |  | 03-42187 |  |  |  |  | 73-99-1702
QUOTATION DATE: | [6 empty] | 1403.05.13 |  | 1403-05-30 |  |  | 1403.05.14 |  | 1403.05.27
NO | DESCRIPTION |  |  | REFERENCE / SPECIFIED |  |  | MEETS REQUISITION REQUIREMENTS
[7 empty] | Bider's Proposal | STATUS | Bider's Proposal |  | STATUS | Bider's Proposal | STATUS | Bider's Proposal | STATUS
1 | Scope of Work And Supply
1.1 | Scope of Work And Supply |  |  | 6 Tags number (P-2206,P-2104,P-2102,P-2103AB,P-2209,P-2203AB) |  |  | A | YES | A |  | YES | A | YES | A | YES
1.3 | All auxiliary systems and components |  |  | Requisition |  |  | A | YES | A |  | YES | A | YES | A | YES
1.4 | Spare parts for pre commissioning and commissioning |  |  | Requisition |  |  | A | YES | A |  | YES | NS | NO | A | YES
1.5 | Spare parts list for two (2) years operation {Option} |  |  | Requisition |  |  | A | YES | A |  | YES | NS | NO | A | YES
1.6 | Capital spare parts {Option} |  |  | Requisition |  |  | A | YES | A |  | YES | NS | NO | A | YES
1.7 | Surface Preparation & Painting |  |  | Requisition |  |  | A | YES | A |  | YES | NS | NO | A | YES
2 | Technical Requirements
2.1 | Applicable of Code & Standards/ Edition |  |  | ISO 5199, IPS-M-PM-115 |  |  | A | YES | A |  | YES | NS | NO | A | YES
2.2 | Material |  |  | Requisition |  |  | A | YES | A |  | YES | NS | NO | A | YES
2.3 | Guarantee Term |  |  | The guarantee period shall be eighteen (18) months from the date of delivery or twelve (12) months from the installation date of each equipment/packages at site. |  |  | A | YES | A |  | YES | NS | NO | A | YES
3 | Document Requirements
3.1 | Documentation |  |  | Requisition |  |  | A (After P.O) | YES | A |  | YES | NS | NO | A (After P.O) | YES
3.2 | Material Test Certificate |  |  | Requisition |  |  | A (After P.O) | YES | A |  | YES | NS | NO | A(After P.O) for main part | YES
4 | Glycol Transfer Pump (P-2103AB)
4.1 | Rated Capacity (m3/h) |  |  | 5.5 |  |  | A | YES | A |  | YES | A | YES | A | YES
4.2 | PumpimgTemp. °C |  |  | 50 |  |  | A | YES | A |  | YES | A | YES | A | YES
4.3 | Diff. Head(m) |  |  | 18.3 |  |  | A | YES | A |  | YES | A | YES | 18.5 | YES
4.4 | Nominal power (Kw) |  |  | VTS |  |  | 5.5 | YES | 1.1 |  | YES | 4 | YES | 1.5 | YES
4.5 | Material |  |  | S-8 |  |  | A | YES | A |  | YES | A | YES | A | YES
4.6 | NPSHA (m) |  |  | 9.9 |  |  | A | YES | A |  | YES | A | YES | A | YES
4.7 | NPSHr (m) |  |  | VTS |  |  | 1 | YES | 1 |  | YES | 1.5 | YES | 0.7 | YES
4.8 | Efficiency (%) |  |  | VTS |  |  | 10 | YES | 28 |  | YES | 30 | YES | 29 | YES
4.9 | Sealing |  |  | 11 |  |  | A | YES | A |  | YES | A | YES | A | YES
4.1 | Area clarification |  |  | ZONE2 /IIA/ T3 |  |  | A | YES | A |  | YES | A | YES | A | YES
4.11 | Type |  |  | OH2 |  |  | A | YES | A |  | YES | A | YES | A | YES
5 | Glycol Manual Pump(2102)
5.1 | Rated Capacity (m3/h) |  |  | 3.3 |  |  | A | YES | A |  | YES | A | YES | 3.5 | YES
5.2 | PumpimgTemp. °C |  |  | 50 |  |  | A | YES | A |  | YES | A | YES | A | YES
5.3 | Diff. Head |  |  | 13.7 |  |  | A | YES | A |  | YES | A | YES | 14 | YES
5.4 | Nominal power (Kw) |  |  | VTS |  |  | 4 | YES | 1.1 |  | YES | 3 | YES | 1.1 | YES
5.5 | Material |  |  | S-8 |  |  | A | YES | A |  | YES | A | YES | A | YES
5.6 | NPSHA |  |  | 9.2 |  |  | A | YES | A |  | YES | A | YES | A | YES
5.7 | NPSHr |  |  | VTS |  |  | 1 | YES | 0.25 |  | YES | 1.7 | YES | 0.7 | YES
5.8 | Efficiency |  |  | VTS |  |  | 19 | YES | 30 |  | YES | NS | NO | 20 | YES
5.9 | Sealing |  |  | 11 |  |  | A | YES | A |  | YES | A | YES | A | YES
5.1 | Area clarification |  |  | Zone 2 /IIA/ T4 |  |  | A | YES | A |  | YES | A | YES | A | YES
5.11 | Type |  |  | OH2 |  |  | A | YES | A |  | YES | A | YES | A | YES
6 | SUMP PUMPS(P-2203 AB)
6.1 | Rated Capacity (m3/h) |  |  | 5.5 |  |  | A | YES | A |  | YES | A | YES | A | YES
6.2 | PumpimgTemp. °C |  |  | 50 |  |  | A | YES | A |  | YES | A | YES | A | YES
6.3 | Diff. Head |  |  | 19.9 |  |  | 19.9+4 (Pump Length) | YES | A |  | YES | A | YES | 20 | YES
6.4 | Nominal power (Kw) |  |  | VTS |  |  | 5.5 | YES | 2.2 |  | YES | 2.2 | YES | 1.5 | YES
6.5 | Material |  |  | I-2 |  |  | A | YES | A |  | YES | A | YES | A | YES
6.6 | NPSHA |  |  | 9.4 |  |  | A | YES | A |  | YES | A | YES | A | YES
6.7 | NPSHr |  |  | VTS |  |  | 0.61 | YES | 1.5 |  | YES | NS | NO | 0.5 | YES
6.8 | Efficiency |  |  | VTS |  |  | 18 | YES | 28 |  | YES | 28 | YES | 31 | YES
6.9 | Sealing |  |  | 11+61 |  |  | 13+61 | YES | A |  | YES | A | YES | A | YES
6.1 | Area clarification |  |  | Zone 1 / IIB / T3 |  |  | A | YES | A |  | YES | A | YES | A | YES
6.11 | Type |  |  | VS4 |  |  | VS1 | YES | A |  | YES | A | YES | A | YES
7 | Potable Water Pump (P-2209)
7.1 | Rated Capacity (m3/h) |  |  | 5.5 |  |  | A | YES | A |  | YES | A | YES | A | YES
7.2 | PumpimgTemp. °C |  |  | 50 |  |  | A | YES | A |  | YES | A | YES | A | YES
7.3 | Diff. Head |  |  | 29.9 |  |  | A | YES | A |  | YES | A | YES | 30 | YES
7.4 | Nominal power (Kw) |  |  | VTS |  |  | 4 | YES | 1.1 |  | YES | 4 | YES | 3 | YES
7.5 | Material |  |  | I-2 |  |  | A | YES | A |  | YES | A | YES | A | YES
7.6 | NPSHA |  |  | 8.6 |  |  | A | YES | A |  | YES | A | YES | A | YES
7.7 | NPSHr |  |  | VTS |  |  | 1.05 | YES | 0.5 |  | YES | 4.5 | YES | 0.5 | YES
7.8 | Efficiency |  |  | VTS |  |  | 28 | YES | 32 |  | YES | 25 | YES | 20 | YES
7.9 | Sealing |  |  | 11 |  |  | A | YES | A |  | YES | A | YES | A | YES
7.1 | Area clarification |  |  | SAFE |  |  | A | YES | A |  | YES | A | YES | A | YES
7.11 | Type |  |  | OH2 |  |  | A | YES | A |  | YES | A | YES | A | YES
8 | Diesel Pump (P-2206)
8.1 | Rated Capacity (m3/h) |  |  | 5.5+min flow |  |  | A | YES | 6 |  | YES | A | YES | A | YES
8.2 | PumpimgTemp. °C |  |  | 50 |  |  | A | YES | A |  | YES | A | YES | A | YES
8.3 | Diff. Head |  |  | 24 |  |  | A | YES | A |  | YES | A | YES | A | YES
8.4 | Nominal power (Kw) |  |  | VTS |  |  | 4 | YES | 1.1 |  | YES | 3 | YES | 2.2 | YES
8.5 | Material |  |  | S-1 |  |  | A | YES | A |  | YES | A | YES | A | YES
8.6 | NPSHA |  |  | 10 |  |  | A | YES | A |  | YES | A | YES | A | YES
8.7 | NPSHr |  |  | VTS |  |  | 1.05 | YES | 0.7 |  | YES | 4.6 | YES | 0.5 | YES
8.8 | Efficiency |  |  | VTS |  |  | 39 | YES | 31 |  | YES | 30 | YES | 20 | YES
8.9 | Sealing |  |  | 11 |  |  | A | YES | A |  | YES | A | YES | A | YES
8.1 | Area clarification |  |  | SAFE |  |  | A | YES | A |  | YES | A | YES | A | YES
8.11 | Type |  |  | OH2 |  |  | A | YES | A |  | YES | A | YES | A | YES
9 | Glycol Drain Pump (P-2104)
9.1 | Rated Capacity (m3/h) |  |  | 3.3 |  |  | A | YES | A |  | YES | A | YES | A | YES
9.2 | PumpimgTemp. °C |  |  | 50 |  |  | A | YES | A |  | YES | A | YES | A | YES
9.3 | Diff. Head |  |  | 18.3 |  |  | 18.3+1 (Pump Length) | YES | A |  | YES | A | YES | 19 | YES
9.4 | Nominal power (Kw) |  |  | VTS |  |  | 7.5 | YES | 1.1 |  | YES | 5.5 | YES | 1.1 | YES
9.5 | Material |  |  | S-8 |  |  | A | YES | A |  | YES | A | YES | A | YES
9.6 | NPSHA |  |  | 10.4 |  |  | A | YES | A |  | YES | A | YES | A | YES
9.7 | NPSHr |  |  | VTS |  |  | 1.05 | YES | 0.1 |  | YES | NS | YES | 0.5 | YES
9.8 | Efficiency |  |  | VTS |  |  | 11.5 | YES | 25 |  | YES | 25 | YES | 25 | YES
9.9 | Sealing |  |  | 11 |  |  | A | YES | 13 |  | YES | 14 | YES | A | YES
9.1 | Area clarification |  |  | Zone 1/ IIB/ T3 |  |  | A | YES | A |  | YES | A | YES | A | YES
9.11 | Type |  |  | VS4 |  |  | A | YES | A |  | YES | A | YES | A | YES
10 | Delivery Time | [5 empty] | 8 months |  | 180 Working Day |  |  | NS |  | 6 months
11 | Manufacturer's Location | [5 empty] | Tabriz |  | Tehran |  |  | TABRIZ |  | Tehran
General Technical acceptance of Quotation | [6 empty] | ACCEPTED |  | ACCEPTED |  |  | ACCEPTED |  | ACCEPTED
ABBREVIATIONS: A: ACCEPTED By Vendor N: NOT ACCEPTED By Vendor NA:Not Applicable NS:Not Specified C:Clarification Required VTS: Vendor to Specify
Note-1) Please see all Technical Clarification Letters/Technical Documents with vendors attached to TBE.