| # | Clarification Title | Clarification Description (Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.02) | Conclusion (Rev.02) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ELECTRICAL |  |  |  |  |  |  |  |  |
|  | Certificate | The validity certificates for type test of cables shall be submitted by vendor. | Confirmed. as attached |  |  |  |  |
|  | Stamp | All of documents such as MR and technical specification that received from purchaser shall be stamped and returned. | Confirmed. as attached |  |  |  |  |
|  | Catalogue | Relevant catalogues shall be submitted. | Confirmed. as attached |  |  |  |  |
|  | Sub Vendor | Sub vendor list with country of origin shall be submitted. | Confirmed. as attached |  |  |  |  |
|  | Drum | Each drum shall have a tag plate with below descriptions: -drum tag number -cable type -cable size -color of conductors - total cable length | Confirmed |  |  |  |  |
|  | Standard | All cables shall be in accordance with IEC standard (Sector/Round shape, Thickness of XLPE/armor/ lead cover,…) | Confirmed |  |  |  |  |
|  | Standard | All cables shall be according to IPS-M-EL-271(2) & IPS-M-EL-272(2). | confirmed except for the deviation list. |  |  |  |  |
|  | Tolerance | The tolerance of cables length shall be 0 % , +5% | Confirmed |  |  |  |  |
|  | Cable Tag | The following information shall be marked on outer sheath of all cables at intervals in each 1m: -Type of cable -Number of conductor and cross section -Rated voltage -Metric marker every meter -Manufacturer’s name -Year of manufacture -Type of insulation -Standard No. | Confirmed |  |  |  |  |
|  | Drum | Cable drums heavier than 1.5 ton sh.all be made of metallic material. It shall be confirmed by vendor. | Confirmed |  |  |  |  |
|  | MTO | Vendor shall follow MTO document “BK-GCS-PEDCO-120-EL-MT-0003”. | Confirmed |  |  |  |  |