| ##### ITEM NO. | TECHNICAL DESCRIPTION | Unit | 3 × 95 / (16) 11kV N2XSEYRY |
| --- | --- | --- | --- |
| 1 | MANUFACTURER’S NAME | - | SIMCO |
| 2 | CABLE TYPE | - | N2XSEYRY |
| 3 | INTERNAL CODE |  | 2209002010 |
| 4 | ABBREVIATED DESCRIPTION |  | Cu / SC / XLPE / SC / WBSC tape / copper wire + copper tape / PVC / SWA / PVC |
| 5 | VOLTAGE RATING (U0/U) | kV | 6 / 10 / 12 |
| 6 | STANDARD | - | IEC 60502-2, IEC 60228, IEC 60332-3-24 (Cat.C) |
| 7 | NUMBER OF CORES | - | 3 |
| 8 | CONDUCTOR: |  |  |
|  | MATERIAL | - | Stranded copper |
|  | SECTIONAL AREA | mm² | 95 |
|  | SHAPE | - | Class 2 (IEC 60228) , Circular compacted |
|  | DIAMETER | mm | 11.3 |
| 9 | CONDUCTOR SCREEN: |  |  |
|  | MATERIAL | - | Extruded semiconductor |
|  | EXTRUDED SEMI-CONDUCTOR THICKNESS | mm | 0.7 |
|  | CURING PROCESS | - | Dry curing |
| 10 | INSULATION: |  |  |
|  | MATERIAL | - | XLPE |
|  | NOMINAL THICKNESS | mm | 3.4 |
|  | APPLICATION METHOD | - | Extruded |
|  | CURING PROCESS | - | Dry curing |
| 11 | INSULATION SCREEN: |  |  |
|  | MATERIAL | - | Semi-conductor |
|  | NOMINAL THICKNESS | mm | 0.5 |
|  | APPLICATION METHOD | - | Extruded |
|  | CURING PROCESS | - | Dry curing |
|  | WATER BLOCKED SEMI-CONDUCTING TAPE THICKNESS | mm | 0.25±0.02 |
| 12 | METALLIC SHIELDING WIRE SCREEN: |  |  |
|  | SHAPE | - | Round wires |
|  | MATERIAL & TYPE | - | Annealed copper wires |
|  | TOTAL CROSS-SECTION | mm² | 16 |
|  | COPPER TAPE DIMENTION | mmxmm | 10 x 0.1 (applied helically over copper wires) |
|  | CORE IDENTIFICATION | - | longitudinally binder tape over each screened core (Red, Yellow, Blue) |
| 13 | INNER SHEATH (BEDDING): |  |  |
|  | MATERIAL | - | Extruded PVC |
|  | THICKNESS | mm | 1.6 |

| ##### ITEM NO. | TECHNICAL DESCRIPTION |  |  | Unit |  | 3 × 95 / (16) 11kV N2XSEYRY (continued) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 14 | ARMORING: |  |  |  |  |  |  |
|  | MATERIAL |  |  | - |  | Galvanized Steel Wire |  |
|  | DIAMETER OF WIRES |  |  | mm |  | 2.5 (Dia. under armor: Approx.51.5) |  |
|  | COVERAGE PERCENT OF ARMOUR WIRES |  |  |  |  | >95% |  |
| 15 | OUTER SHEATH : |  |  |  |  |  |  |
|  | MATERIAL |  |  | - |  | PVC (ST2, UV Resistant, Flame Retardant) |  |
|  | THICKNESS |  |  | mm |  | 3 |  |
|  | COLOR |  |  | - |  | Red |  |
|  | APPLICATION METHOD |  |  | - |  | Extruded |  |
| 16 | APPROX. OVERALL DIAMETER OF COMPLETED CABLE |  |  | mm |  | 62.5 |  |
| 17 | MINIMUM BENDING RADIUS |  |  | mm |  | 940 |  |
| 18 | MAX. PULLING FORCE / PER CABLE |  |  | N |  | 26700 (Acc. to IEEE) |  |
| 19 | APPROX. CABLE WEIGHT |  |  | kg/km |  | 8020 |  |
| 20 | MAX. DC RESISTANCE OF CONDUCOR AT 20°C |  |  | km |  | 0.193 |  |
| 21 | MAX. DC RESISTANCE OF CONDUCOR AT 30°C |  |  | km |  | 0.200 |  |
| 22 | MAX. AC RESISTANCE OF CONDUCOR AT 90°C |  |  | km |  | 0.247 |  |
| 23 | REACTANCE |  |  | km |  | 0.095 |  |
| 24 | CAPACITANCE |  |  | µF/km |  | 0.298 |  |
| 25 | MAX CURRENT RATING OF CABLE IN FOLLOWING CONDITION : |  |  |  |  | Both-ends bonding |  |
|  | DEPTH OF LAYING |  |  | m |  | 0.8 |  |
|  | TERMAL RESISTANCE OF SOIL |  |  | °C.m/W |  | 1.5 |  |
|  | SOIL TEMPERATURE |  |  | °C |  | 20 |  |
|  | AIR TEMPERATURE |  |  | °C |  | 30 |  |
|  | CURRENT RATING IN GROUND |  |  | A |  | 263 |  |
|  | CURRENT RATING IN AIR |  |  | A |  | 307 |  |
| 26 | MAX. SHORT CIRCUIT RATING AT 1 SEC: |  |  |  |  |  |  |
|  | CONDUCTOR INITIAL TEMPERATURE 90ºC AND FINAL TEMPERATURE 250ºC |  |  | kA |  | 13.6 |  |
|  | SCREEN INITIAL TEMPERATURE 50ºC AND FINAL TEMPERATURE 250ºC |  |  | kA |  | 2.64 |  |
| 27 | MAX. CONDUCTOR TEMPERATURE: |  |  |  |  |  |  |
|  | CONTINUOUS CURRENT |  |  | °C |  | 90 |  |
|  | SHORT CIRCUIT |  |  | °C |  | 250 |  |
| NOTES: |  |  |  |  |  |  |  |
|  |  | 2X : XLPE insulation |  |  |  |  | S.C. : Semi-conductor |
|  |  | Y: PVC inner or outer sheath |  |  |  |  | PVC : Polyvinyl Chloride |
|  |  | R: Wire armor |  |  |  |  | XLPE : Cross linked polyethylene |
|  |  | SWA: Steel Wire Armor |  |  |  |  | WBSC tape : Water Blocking Semi Conducting tape |
|  |  | SE : Copper wire screen (plus copper tape applied helically) for each Cores |  |  |  |  |  |

| ##### ITEM NO. | TECHNICAL DESCRIPTION | Unit | 3 × 95 / (16) 11kV N2XSEYKYRY |
| --- | --- | --- | --- |
| 1 | MANUFACTURER’S NAME | - | SIMCO |
| 2 | CABLE TYPE | - | N2XSEYKYRY |
| 3 | INTERNAL CODE |  | 2209007002 |
| 4 | ABBREVIATED DESCRIPTION |  | Cu / SC / XLPE / SC / WBSC tape / Copper wire + Copper tape / PVC / LC / PVC / SWA / PVC |
| 5 | VOLTAGE RATING (U0/U) | kV | 6 / 10 / 12 |
| 6 | STANDARD | - | IEC 60502-2, IEC 60228, IEC 60332-3-24 (Cat.C) |
| 7 | NUMBER OF CORES | - | 3 |
| 8 | CONDUCTOR: |  |  |
|  | MATERIAL | - | Stranded copper |
|  | SECTIONAL AREA | mm² | 95 |
|  | SHAPE | - | Class 2 (IEC 60228) ,Circular compacted |
|  | DIAMETER | mm | 11.3 |
| 9 | CONDUCTOR SCREEN: |  |  |
|  | MATERIAL | - | Extruded semiconductor |
|  | EXTRUDED SEMI-CONDUCTOR THICKNESS | mm | 0.7 |
|  | CURING PROCESS | - | Dry curing |
| 10 | INSULATION: |  |  |
|  | MATERIAL | - | XLPE |
|  | NOMINAL THICKNESS | mm | 3.4 |
|  | APPLICATION METHOD | - | Extruded |
|  | CURING PROCESS | - | Dry curing |
| 11 | INSULATION SCREEN: |  |  |
|  | MATERIAL | - | Semi-conductor |
|  | NOMINAL THICKNESS | mm | 0.5 |
|  | APPLICATION METHOD | - | Extruded |
|  | CURING PROCESS | - | Dry curing |
|  | WATER BLOCKED SEMI-CONDUCTING TAPE THICKNESS | mm | 0.25±0.02 |
| 12 | METALLIC SHIELDING WIRE SCREEN: |  |  |
|  | SHAPE | - | Round wires |
|  | MATERIAL & TYPE | - | Annealed copper wires |
|  | TOTAL CROSS-SECTION | mm² | 16 |
|  | COPPER TAPE DIMENTION | mmxmm | 10 x 0.1 (applied helically over copper wires) |
|  | CORE IDENTIFICATION | - | longitudinally binder tape over each screened core (Red, Yellow, Blue) |
| 13 | INNER COVERING: |  |  |
|  | MATERIAL | - | Extruded PVC |
|  | THICKNESS | mm | 1.6 |
| 14 | METALLIC SHEATH: |  |  |
|  | MATERIAL | - | Lead |
|  | THICKNESS | mm | 2.2(Dia. Over Lead: Approx.56.5) |

| ##### ITEM NO. | TECHNICAL DESCRIPTION |  |  | Unit |  | 3 × 95 / (16) 11kV N2XSEYKYRY (continued) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 15 | INNER SHEATH (BEDDING): |  |  |  |  |  |  |
|  | MATERIAL |  |  | - |  | Extruded PVC |  |
|  | THICKNESS |  |  | mm |  | 1.7 |  |
| 16 | ARMORING: |  |  |  |  |  |  |
|  | MATERIAL |  |  | - |  | Galvanized Steel Wire |  |
|  | DIAMETER OF WIRES |  |  | mm |  | 2.5 (Dia. under armor: Approx.59.5) |  |
|  | COVERAGE PERCENT OF ARMOUR WIRES |  |  |  |  | >95% |  |
| 17 | OUTER SHEATH : |  |  |  |  |  |  |
|  | MATERIAL |  |  | - |  | PVC (ST2, UV Resistant, Flame Retardant) |  |
|  | THICKNESS |  |  | mm |  | 3.3 |  |
|  | COLOR |  |  | - |  | Red |  |
|  | APPLICATION METHOD |  |  | - |  | Extruded |  |
| 18 | APPROX. OVERALL DIAMETER OF COMPLETED CABLE |  |  | mm |  | 71 |  |
| 19 | APPROX. WEIGHT OF CABLE |  |  | kg/km |  | 13290 |  |
| 20 | MINIMUM BENDING RADIUS |  |  | mm |  | 1065 |  |
| 21 | MAX. PULLING FORCE / PER CABLE |  |  | N |  | 26700 (Acc. to IEEE) |  |
| 22 | MAX. DC RESISTANCE OF CONDUCOR AT 20°C |  |  | km |  | 0.193 |  |
| 23 | MAX. DC RESISTANCE OF CONDUCOR AT 30°C |  |  | km |  | 0.200 |  |
| 24 | MAX. AC RESISTANCE OF CONDUCOR AT 90°C |  |  | km |  | 0.247 |  |
| 25 | REACTANCE |  |  | km |  | 0.095 |  |
| 26 | CAPACITANCE |  |  | µF/km |  | 0.298 |  |
| 27 | MAX CURRENT RATING OF CABLE IN FOLLOWING CONDITION : |  |  |  |  | Both-ends bonding |  |
|  | DEPTH OF LAYING |  |  | m |  | 0.8 |  |
|  | TERMAL RESISTANCE OF SOIL |  |  | °C.m/W |  | 1.5 |  |
|  | SOIL TEMPERATURE |  |  | °C |  | 20 |  |
|  | AIR TEMPERATURE |  |  | °C |  | 30 |  |
|  | CURRENT RATING IN GROUND |  |  | A |  | 263 |  |
|  | CURRENT RATING IN AIR |  |  | A |  | 307 |  |
| 28 | MAX. SHORT CIRCUIT RATING AT 1 SEC: |  |  |  |  |  |  |
|  | CONDUCTOR INITIAL TEMPERATURE 90ºC AND FINAL TEMPERATURE 250ºC |  |  | kA |  | 13.6 |  |
|  | SCREEN INITIAL TEMPERATURE 50ºC AND FINAL TEMPERATURE 250ºC |  |  | kA |  | 2.64 |  |
| 29 | MAX. CONDUCTOR TEMPERATURE: |  |  |  |  |  |  |
|  | CONTINUOUS CURRENT |  |  | °C |  | 90 |  |
|  | SHORT CIRCUIT |  |  | °C |  | 250 |  |
| NOTES: |  |  |  |  |  |  |  |
|  |  | 2X : XLPE insulation |  |  |  |  | PVC : Polyvinyl Chloride |
|  |  | Y: PVC inner or outer sheath |  |  |  |  | XLPE : Cross linked polyethylene |
|  |  | R: Wire armor |  |  |  |  | LC : lead Cover |
|  |  | SWA: Steel Wire Armor |  |  |  |  | K: Metallic lead sheath |
|  |  | WBSC Tape : Water blocked Semi-Conducting tape |  |  |  |  | S.C. : Semi-conductor |
|  |  | S : Copper wire screen (plus copper tape applied helically) |  |  |  |  |  |

| ITEM NO. | TECHNICAL DESCRIPTION | Unit | 3 × 95 / (16) 6kV N2XSEYRY |
| --- | --- | --- | --- |
| 1 | MANUFACTURER’S NAME | - | SIMCO |
| 2 | CABLE TYPE | - | N2XSEYRY |
| 3 | INTERNAL CODE |  | 2208402014 |
| 4 | ABBREVIATED DESCRIPTION | - | Cu / SC / XLPE / SC / WBSC tape / Copper Wire + Copper Tape / PVC / SWA / PVC |
| 5 | VOLTAGE RATING (U0/U/Um) | kV | 3.6 / 6 / 7.2 |
| 6 | STANDARD | - | IEC 60502-2, IEC 60228, IEC 60332-3-24 (Cat.C) |
| 7 | NUMBER OF CORES | - | 3 |
| 8 | CONDUCTOR: |  |  |
|  | MATERIAL | - | Plain annealed stranded copper |
|  | SECTIONAL AREA | mm² | 95 |
|  | SHAPE | - | Class 2 (IEC 60228) , Circular compacted |
|  | DIAMETER | mm | 11.3 |
| 9 | CONDUCTOR SCREEN: |  |  |
|  | MATERIAL | - | Extruded semiconductor |
|  | EXTRUDED SEMI-CONDUCTOR THICKNESS | mm | 0.7 |
|  | CURING PROCESS | - | Dry curing |
| 10 | INSULATION: |  |  |
|  | MATERIAL | - | XLPE |
|  | NOMINAL THICKNESS | mm | 2.5 |
|  | APPLICATION METHOD | - | Extruded |
|  | CURING PROCESS | - | Dry curing |
| 11 | INSULATION SCREEN: |  |  |
|  | MATERIAL | - | Semi-conductor |
|  | NOMINAL THICKNESS | mm | 0.5 |
|  | APPLICATION METHOD | - | Extruded |
|  | CURING PROCESS | - | Dry curing |
|  | WATER BLOCKED SEMI-CONDUCTING TAPE THICKNESS | mm | 0.25±0.02 |
| 12 | METALLIC SHIELDING WIRE SCREEN: |  |  |
|  | SHAPE | - | Round wires |
|  | MATERIAL & TYPE | - | Annealed copper wires |
|  | TOTAL CROSS-SECTION | mm² | 16 |
|  | COPPER TAPE DIMENSION | mmxmm | 10 x 0.1 (applied helically over copper wires) |
|  | CORE IDENTIFICATION | - | longitudinally binder tape over each screened core (Red, Yellow, Blue) |
| 13 | BEDDING(INNER SHEATH): |  |  |
|  | MATERIAL | - | Extruded PVC |
|  | THICKNESS | mm | 1.5 |

| ITEM NO. | TECHNICAL DESCRIPTION |  | Unit | 3 × 95 / (16) 6kV N2XSEYRY (continued) |
| --- | --- | --- | --- | --- |
| 14 | ARMORING: |  |  |  |
|  | MATERIAL |  | - | One layer of Galvanized Steel Wires |
|  | DIAMETER OF WIRES |  | mm | 2.5 (Dia. under armor: Approx.47.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | - | > 95% |
| 15 | OUTER SHEATH : |  |  |  |
|  | MATERIAL |  | - | PVC (ST2, UV Resistant, Flame Retardant) |
|  | THICKNESS |  | mm | 2.8 |
|  | COLOR |  | - | Red |
|  | APPLICATION METHOD |  | - | Extruded |
| 16 | APPROX. OVERALL DIAMETER OF COMPLETED CABLE |  | mm | 58 |
| 17 | MINIMUM BENDING RADIUS |  | mm | 870 |
| 18 | MAX. PULLING FORCE |  | N | 26700 (Acc. to IEEE) |
| 19 | APPROX. WEIGHT OF CABLE |  | kg/km | 7395 |
| 20 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C |  | km | 0.193 |
| 21 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C |  |  | 0.200 |
| 22 | MAX. AC RESISTANCE OF CONDUCTOR AT 90°C |  | km | 0.247 |
| 23 | REACTANCE |  | km | 0.089 |
| 24 | CAPACITANCE |  | µF/km | 0.358 |
| 25 | MAX CURRENT RATING OF CABLE IN FOLLOWING CONDITION : |  |  | Both-ends bonding |
|  | DEPTH OF LAYING |  | m | 0.8 |
|  | THERMAL RESISTANCE OF SOIL |  | °C.m/W | 1.5 |
|  | SOIL TEMPERATURE |  | °C | 20 |
|  | AIR TEMPERATURE |  | °C | 30 |
|  | CURRENT RATING IN GROUND |  | A | 263 |
|  | CURRENT RATING IN AIR |  | A | 307 |
| 26 | MAX. SHORT CIRCUIT RATING AT 1 SEC |  |  |  |
|  | CONDUCTOR INITIAL TEMPERATURE 90ºC AND FINAL TEMPERATURE 250ºC |  | kA | 13.6 |
|  | SCREEN INITIAL TEMPERATURE 50ºC AND FINAL TEMPERATURE 250ºC |  | kA | 2.64 |
|  | MAX. CONDUCTOR TEMPERATURE: |  |  |  |
|  | CONTINUOUS CURRENT |  | °C | 90 |
|  | SHORT CIRCUIT |  | °C | 250 |
| NOTES: |  |  |  |  |
|  | 2X : XLPE insulation |  |  | S.C. : Semi-conductor |
|  | Y: PVC inner or outer sheath |  |  | PVC : Polyvinyl Chloride |
|  | SE : Copper wire screen (plus copper tape applied helically) for each core |  |  | XLPE : Cross linked polyethylene |
|  | R: Wire armor |  |  | WBSC tape : Water Blocking Semi Conducting tape |
|  | SWA: Steel Wire armor |  |  |  |

| ##### ITEM NO. | TECHNICAL DESCRIPTION | Unit | 1 × 95 / 16 6kV N2XSYRY |
| --- | --- | --- | --- |
| 1 | MANUFACTURER’S NAME | - | SIMCO |
| 2 | CABLE TYPE | - | N2XSYRY |
| 3 | INTERNAL CODE |  | 2208401005 |
| 4 | ABBREVIATED DESCRIPTION | - | Cu / SC / XLPE / SC / WBSC tape / copper wire + copper tape / PET / PVC / AWA / PVC |
| 5 | VOLTAGE RATING (U0/U/Um) | kV | 3.6 / 6 / 7.2 |
| 6 | STANDARD | - | IEC 60502-2, IEC 60228, IEC 60332-3-24 (Cat.C) |
| 7 | NUMBER OF CORES | - | 1 |
| 8 | CONDUCTOR: |  |  |
|  | MATERIAL | - | Stranded copper |
|  | SECTIONAL AREA | mm² | 95 |
|  | SHAPE | - | Class 2 (IEC 60228) , Circular compacted |
|  | DIAMETER | mm | 11.3 |
| 9 | CONDUCTOR SCREEN: |  |  |
|  | MATERIAL | - | Extruded semiconductor |
|  | EXTRUDED SEMI-CONDUCTOR THICKNESS | mm | 0.7 |
|  | CURING PROCESS | - | Dry curing |
| 10 | INSULATION: |  |  |
|  | MATERIAL | - | XLPE |
|  | NOMINAL THICKNESS | mm | 2.5 |
|  | APPLICATION METHOD | - | Extruded |
|  | CURING PROCESS | - | Dry curing |
| 11 | INSULATION SCREEN: |  |  |
|  | MATERIAL | - | Semi-conductor |
|  | NOMINAL THICKNESS | mm | 0.5 |
|  | APPLICATION METHOD | - | Extruded |
|  | CURING PROCESS | - | Dry curing |
|  | WATER BLOCKED SEMI-CONDUCTING TAPE THICKNESS | mm | 0.25±0.02 |
| 12 | METALLIC SHIELDING WIRE SCREEN: |  |  |
|  | SHAPE | - | Round wires |
|  | MATERIAL & TYPE | - | Annealed copper wires |
|  | EQUIVALENT CROSS-SECTION | mm² | 16 |
|  | COPPER TAPE DIMENTION | mmxmm | 10 x 0.1 (applied helically over copper wires) |
| 13 | POLYESTER TAPE THICKNESS | mm | 0.05 |
| 14 | BEDDING: |  |  |
|  | MATERIAL | - | Extruded PVC |
|  | THICKNESS | mm | 1.2 |

| ##### ITEM NO. | TECHNICAL DESCRIPTION |  | Unit | 1 × 95 / 16 6kV N2XSYRY (continued) |  |
| --- | --- | --- | --- | --- | --- |
| 15 | ARMORING: |  |  |  |  |
|  | MATERIAL |  | - | Aluminum wires |  |
|  | DIAMETER OF WIRES |  | mm | 1.60 (Dia. under armor: Approx.24) |  |
|  | COVERAGE PERCENT OF ARMOUR WIRES |  |  | >95 % |  |
| 16 | OUTER SHEATH : |  |  |  |  |
|  | MATERIAL |  | - | PVC (ST2, UV Resistant, Flame Retardant) |  |
|  | THICKNESS |  | mm | 1.9 |  |
|  | COLOR |  | - | Red |  |
|  | APPLICATION METHOD |  | - | Extruded |  |
| 17 | APPROX. OVERALL DIAMETER OF COMPLETED CABLE |  | mm | 31 |  |
| 18 | MINIMUM BENDING RADIUS |  | mm | 465 |  |
| 19 | MAX. PULLING FORCE / PER CABLE |  | N | 8650 |  |
| 20 | APPROX. WEIGHT OF CABLE |  | kg/km | 1820 |  |
| 21 | MAX. DC RESISTANCE OF CONDUCOR AT 20°C |  | km | 0.193 |  |
| 22 | MAX. DC RESISTANCE OF CONDUCOR AT 30°C |  | km | 0.200 |  |
| 23 | MAX. AC RESISTANCE OF CONDUCOR AT 90°C |  | km | Trefoil : 0.247 Flat : 0.246 |  |
| 24 | REACTANCE |  | km | Trefoil : 0.115 Flat : 0.204 |  |
| 25 | CAPACITANCE |  | µF/km | 0.385 |  |
| 26 | MAX CURRENT RATING OF CABLE IN FOLLOWING CONDITION : |  |  | Both-ends bonding |  |
|  | DEPTH OF LAYING |  | m | 0.8 |  |
|  | TERMAL RESISTANCE OF SOIL |  | °C.m/W | 1.5 |  |
|  | SOIL TEMPERATURE |  | °C | 20 |  |
|  | AIR TEMPERATURE |  | °C | 30 |  |
|  | CURRENT RATING IN GROUND |  | A | Trefoil : 285 , Flat : 293 |  |
|  | CURRENT RATING IN AIR |  | A | Trefoil : 361 , Flat : 434 |  |
| 27 | MAX. SHORT CIRCUIT RATING AT 1 SEC |  |  |  |  |
|  | CONDUCTOR INITIAL TEMPERATURE 90ºC AND FINAL TEMPERATURE 250ºC |  | kA | 13.6 |  |
|  | SCREEN INITIAL TEMPERATURE 50ºC AND FINAL TEMPERATURE 250ºC |  | kA | 2.64 |  |
| 28 | MAX. CONDUCTOR TEMPERATURE: |  |  |  |  |
|  | CONTINUOUS CURRENT |  | °C | 90 |  |
|  | SHORT CIRCUIT |  | °C | 250 |  |
| NOTES: |  |  |  |  |
|  | 2X : XLPE insulation |  |  | S.C. : Semi-conductor |
|  | S : Copper wire screen (plus copper tapes applied helically) |  |  | PVC : Polyvinyl Chloride |
|  | Y: PVC inner or outer sheath |  |  | XLPE : Cross linked polyethylene |
|  | PET: Polyester tape |  |  | R: Wire armor |
|  | WBSC Tape : Water blocked Semi-Conducting Tape |  |  | AWA: Aluminum Wire Armor |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×4 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116616009 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 4, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 2.3 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead / 1.2 (Dia. Over Lead: Approx.16) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.18) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 24.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 4.61 |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 4.79 |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 5.88 |
| 19 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 52 |
| 20 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 42 |
| 21 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 0.57 |
| 22 | MINIMUM BENDING RADIUS (mm) |  | 295 |
| 23 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 5275 |
| 24 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 25 | APPROX. CABLE WEIGHT (kg/km) |  | 1690 |
| 26 | REACTANCE (Ω/km) |  | 0.099 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner or outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×6 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116616010 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 6, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.7 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead / 1.2 (Dia. Over Lead: Approx.16) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.18) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 24.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 3.08 |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 3.20 |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 3.93 |
| 19 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 64 |
| 20 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 53 |
| 21 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 0.86 |
| 22 | MINIMUM BENDING RADIUS (mm) |  | 295 |
| 23 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 5405 |
| 24 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 25 | APPROX. CABLE WEIGHT (kg/km) |  | 1725 |
| 26 | REACTANCE (Ω/km) |  | 0.094 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner or outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×10 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116616011 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 10, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead / 1.2 (Dia. Over Lead: Approx.16.5) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.18.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 25 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/Km) |  | 1.83 |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 1.90 |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 2.33 |
| 19 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 86 |
| 20 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 73 |
| 21 | 1 SEC DURATION SHORT TIME RATING OF CORES (KA) |  | 1.43 |
| 22 | MINIMUM BENDING RADIUS (mm) |  | 300 |
| 23 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 5625 |
| 24 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 25 | APPROX. CABLE WEIGHT (kg/km) |  | 1885 |
| 26 | REACTANCE (Ω/km) |  | 0.093 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC bedding and outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×16 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116616012 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 16, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead /1.2 (Dia. Over Lead: Approx.18.5) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.20.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 27 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 1.15 |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 1.90 |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 1.47 |
| 19 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 111 |
| 20 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 96 |
| 21 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 2.29 |
| 22 | MINIMUM BENDING RADIUS (mm) |  | 325 |
| 23 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 6565 |
| 24 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 25 | APPROX. CABLE WEIGHT (kg/km) |  | 2250 |
| 26 | REACTANCE (Ω/km) |  | 0.088 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner or outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | TECHNICAL DESCRIPTION |  | ## 3×25 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116616013 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 25, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.9 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead /1.3 (Dia. Over Lead: Approx. 22.5) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx. 24.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 2 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 31.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/Km) |  | 0.727 |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.755 |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 0.927 |
| 19 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 143 |
| 20 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 130 |
| 21 | 1 SEC DURATION SHORT TIME RATING OF CORES (KA) |  | 3.57 |
| 22 | MINIMUM BENDING RADIUS (mm) |  | 380 |
| 23 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 8930 |
| 24 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 25 | APPROX. CABLE WEIGHT (kg/km) |  | 3005 |
| 26 | REACTANCE (Ω/km) |  | 0.082 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | TECHNICAL DESCRIPTION |  | ## 4×10 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116616014 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 10 , class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 4 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue, Black |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.2 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead /1.2 (Dia. Over Lead: Approx.17.7) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.19.7) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 26.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 1.83 |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 1.90 |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 2.33 |
| 19 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 86 |
| 20 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 73 |
| 21 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 1.43 |
| 22 | MINIMUM BENDING RADIUS (mm) |  | 320 |
| 23 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 6320 |
| 24 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 25 | APPROX. CABLE WEIGHT (kg/km) |  | 2110 |
| 26 | REACTANCE (Ω/km) |  | 0.093 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner or outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 4×25 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116616015 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 25, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 4 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.9 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue, Black |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.2 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead /1.4 (Dia. Over Lead: Approx.25.5) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.2 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 2 (Dia. under armor: Approx.27.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 2.1 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 35.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/Km) |  | 0.727 |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.755 |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 0.927 |
| 19 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 143 |
| 20 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 130 |
| 21 | 1 SEC DURATION SHORT TIME RATING OF CORES (KA) |  | 3.58 |
| 22 | MINIMUM BENDING RADIUS (mm) |  | 430 |
| 23 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 11345 |
| 24 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 25 | APPROX. CABLE WEIGHT (kg/km) |  | 3860 |
| 26 | REACTANCE (Ω/km) |  | 0.082 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC bedding and outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | TECHNICAL DESCRIPTION |  | ## 4×50 SM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116806009 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Sector Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 50 , class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 4 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 1 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue, Black |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead /1.5 (Dia. Over Lead: Approx.29) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.2 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 2 (Dia. under armor: Approx.31.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 2.2 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 39.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/Km) |  | 0.387 |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.402 |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 0.494 |
| 19 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 205 |
| 20 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 195 |
| 21 | 1 SEC DURATION SHORT TIME RATING OF CORES (KA) |  | 7.15 |
| 22 | MINIMUM BENDING RADIUS (mm) |  | 475 |
| 23 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 14045 |
| 24 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 25 | APPROX. CABLE WEIGHT (kg/km) |  | 5155 |
| 26 | REACTANCE (Ω/km) |  | 0.076 |
| Notes: |  |  |  |
| SM: Sector stranded conductor |  | R: Round wire armor |  |
| Y: PVC outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | TECHNICAL DESCRIPTION |  | 3×25+16 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116616016 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 25(Phase), 16(Neutral), Class 2 (IEC 60228) |
| 8 | NO.OF CORES |  | 3½ |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.9 (For Core 25) XLPE / 0.7 (For Core 16) |
|  | CORE INSULATION COLORS |  | Red, Yellow, Blue, Black for neutral core |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead / 1.3 (Dia. Over Lead: Approx.24) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx. 26) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 2 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 33 |
| III. ELECTRICAL & MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°c (Ω/km) |  | 0.727 (For Core 25) 1.15 (For Core 16) |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.756 (For Core 25) 1.19 (For Core 16) |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 90°c (Ω/km) |  | 0.927 (For Core 25) 1.47 (For Core 16) |
| 19 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC(A) |  | 143 |
| 20 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 130 |
| 21 | 1 SEC. DURATION SHORT TIME RATING OF CORES (KA) |  | 3.57 (For Core 25) 2.29 (For Core 16) |
| 22 | MINIMUM BENDING RADIUS (mm) |  | 395 |
| 23 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 9800 |
| 24 | MAX. CONDUCTOR TEMPERATURE: |  |  |
|  | AT CONTINUOUS RATING (°C) |  | 90 |
|  | AT SHORT CIRCUIT (°C) |  | 250 |
| 25 | APPROX. CABLE WEIGHT (kg/km) |  | 3300 |
| 26 | REACTANCE (Ω/km) |  | 0.082 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner & outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  | RM: Circular stranded conductor |  |

| ITEM NO. | TECHNICAL DESCRIPTION |  | 3×50+25 (SM/RM) |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116705003 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 50 (Phase-Sector), 25 (Neutral-Circular), Class 2 (IEC 60228) |
| 8 | NO.OF CORES |  | 3½ |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 1 (For Core 50) XLPE / 0.9 (For Core 25) |
|  | CORE INSULATION COLORS |  | Red, Yellow, Blue, Black for neutral core |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead / 1.4 (Dia. Over Lead: Approx.28) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 2 (Dia. under armor: Approx.30) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 2.2 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 38 |
| III. ELECTRICAL & MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°c (Ω/km) |  | 0.387 (For Core 50) 0.727 (For Core 25) |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.402 (For Core 50) 0.756 (For Core 25) |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 90°c (Ω/km) |  | 0.494 (For Core 50) 0.927 (For Core 25) |
| 19 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC(A) |  | 205 |
| 20 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 195 |
| 21 | 1 SEC. DURATION SHORT TIME RATING OF CORES (kA) |  | 7.15 (For Core 50) 3.57 (For Core 25) |
| 22 | MINIMUM BENDING RADIUS (mm) |  | 460 |
| 23 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 13000 |
| 24 | MAX. CONDUCTOR TEMPERATURE: |  |  |
|  | AT CONTINUOUS RATING (°C) |  | 90 |
|  | AT SHORT CIRCUIT (°C) |  | 250 |
| 25 | APPROX. CABLE WEIGHT (kg/km) |  | 4685 |
| 26 | REACTANCE (Ω/km) |  | 0.076 |
| Notes: |  |  |  |
| SM: Stranded sector shaped conductor |  | R: Round wire armor |  |
| Y: PVC outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  | RM: Circular stranded conductor |  |

| ITEM NO. | TECHNICAL DESCRIPTION |  | 3×70+35 (SM/RM) |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116705004 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 70 (Phase-Sector), 35 (Neutral-Circular), Class 2 (IEC 60228) |
| 8 | NO.OF CORES |  | 3½ |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 1.1 (For Core 70) XLPE / 0.9 (For Core 35) |
|  | CORE INSULATION COLORS |  | Red, Yellow, Blue, Black for neutral core |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead / 1.5 (Dia. Over Lead: Approx.31) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 2 (Dia. under armor: Approx.33.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 2.3 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 42 |
| III. ELECTRICAL & MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°c (Ω/km) |  | 0.268 (For Core 70) 0.524 (For Core 35) |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.279 (For Core 70) 0.544 (For Core 35) |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 90°c (Ω/km) |  | 0.342 (For Core 70) 0.662 (For Core 35) |
| 19 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC(A) |  | 252 |
| 20 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 247 |
| 21 | 1 SEC. DURATION SHORT TIME RATING OF CORES (KA) |  | 10 (For Core 70) 5 (For Core 35) |
| 22 | MINIMUM BENDING RADIUS (mm) |  | 505 |
| 23 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 15880 |
| 24 | MAX. CONDUCTOR TEMPERATURE: |  |  |
|  | AT CONTINUOUS RATING (°C) |  | 90 |
|  | AT SHORT CIRCUIT (°C) |  | 250 |
| 25 | APPROX. CABLE WEIGHT (kg/km) |  | 5895 |
| 26 | REACTANCE (Ω/km) |  | 0.075 |
| Notes: |  |  |  |
| SM: Stranded sector shaped copper conductor |  | R: Round wire armor |  |
| Y: PVC outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  | RM: Circular stranded conductor |  |

| ITEM NO. | TECHNICAL DESCRIPTION |  | 3×95+50 SM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116806010 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Sector stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 95 (Phase) , 50 (Neutral) , Class 2 (IEC 60228) |
| 8 | NO.OF CORES |  | 3½ |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 1.1 (For Core 95) XLPE / 1 (For Core 50) |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue, Black for neutral core |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead / 1.7 (Dia. Over Lead: Approx.35.5) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.3 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 2.5 (Dia. under armor: Approx.38) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC(Flame Retardant) / 2.5 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 48 |
| III. ELECTRICAL & MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°c (Ω/Km) |  | 0.193 (For Core 95) 0.387 (For Core 50) |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.201 (For Core 95) 0.402 (For Core 50) |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 90°c (Ω/Km) |  | 0.247 (For Core 95) 0.494 (For Core 50) |
| 19 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC(A) |  | 303 |
| 20 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 305 |
| 21 | 1 SEC. DURATION SHORT TIME RATING OF CORES (KA) |  | 13.6 (For Core 95) 7.15 (For Core 50) |
| 22 | MINIMUM BENDING RADIUS (mm) |  | 575 |
| 23 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 20740 |
| 24 | MAX. CONDUCTOR TEMPERATURE: |  |  |
|  | AT CONTINUOUS RATING (°C) |  | 90 |
|  | AT SHORT CIRCUIT (°C) |  | 250 |
| 25 | APPROX. CABLE WEIGHT (kg/km) |  | 7985 |
| 26 | REACTANCE (Ω/km) |  | 0.074 |
| Notes: |  |  |  |
| SM: Sector stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner or outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×120+70 SM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116806011 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Sector Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 120 (Phase), 70 (Neutral), Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3½ |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 1.2 (For Core 120) XLPE / 1.1 (For Core 70) |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue, Black for neutral core |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead / 1.7 (Dia. Over Lead: Approx.38.5) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.4 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 2.5 (Dia. under armor: Approx.41.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 2.6 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 51.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/Km) |  | 0.153 (For Core 120) 0.268 (For Core 70) |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.159 (For Core 120) 0.279 (For Core 70) |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 0.196 (For Core 120) 0.342 (For Core 70) |
| 19 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 346 |
| 20 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 355 |
| 21 | 1 SEC DURATION SHORT TIME RATING OF CORES (KA) |  | 17.17 (For Core 120) 10 (For Core 70) |
| 22 | MINIMUM BENDING RADIUS (mm) |  | 618 |
| 23 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 23870 |
| 24 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 25 | APPROX. CABLE WEIGHT (kg/km) |  | 9310 |
| 26 | REACTANCE (Ω/km) |  | 0.072 |
| Notes: |  |  |  |
| SM: Sector stranded conductor |  | R: Round wire armor |  |
| Y: PVC bedding and outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×4 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116607003 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (CAT.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 4, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.25 (Dia. under armor: Approx.11) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 17 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 4.61 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 4.79 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 5.88 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 52 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 42 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 0.572 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 205 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 2600 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 610 |
| 24 | REACTANCE (Ω/km) |  | 0.099 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner & outer sheath |  | SWA: Steel Wire Armor |  |
| PVC : Polyvinyl chloride |  |  |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×35 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116607008 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 35, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.9 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.22.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.9 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 29.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 0.524 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.545 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 0.669 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 173 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 160 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 5 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 355 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 7835 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 2200 |
| 24 | REACTANCE (Ω/km) |  | 0.077 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner & outer sheath |  | SWA: Steel Wire Armor |  |
| PVC : Polyvinyl chloride |  |  |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×185 SM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116804006 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Sector Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 185, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 1.6 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.3 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 2.5 (Dia. under armor: Approx.40) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 2.6 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 50 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 0.0991 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.1029 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 0.128 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 441 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 469 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 26.5 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 600 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 22500 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 8015 |
| 24 | REACTANCE (Ω/km) |  | 0.073 |
| Notes: |  |  |  |
| SM: Sector shaped stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner & outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  |  |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 4×4 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116607010 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (CAT.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 4, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 4 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue, Black |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.25 (Dia. under armor: Approx.12) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 18 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/Km) |  | 4.61 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 4.79 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 5.88 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 52 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 42 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (KA) |  | 0.572 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 220 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 2920 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 685 |
| 24 | REACTANCE (Ω/km) |  | 0.099 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner & outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  |  |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 4×10 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116607012 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (CAT.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 10, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 4 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue, Black |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.25 (Dia. under armor: Approx.16) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 22 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 1.83 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 1.90 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 2.33 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 86 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 73 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 1.43 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 265 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 4360 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 1060 |
| 24 | REACTANCE (Ω/km) |  | 0.093 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner or outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  |  |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 4×16 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116607013 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (CAT.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 16, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 4 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue, Black |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.18.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 25 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 1.15 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 1.20 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 1.47 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 111 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 96 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 2.29 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 300 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 5625 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 1510 |
| 24 | REACTANCE (Ω/km) |  | 0.088 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner & outer sheath |  | SWA: Steel Wire Armor |  |
| PVC : Polyvinyl chloride |  |  |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 4×25 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116607014 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (CAT.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 25, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 4 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.9 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue, Black |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.22) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.9 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 29 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 0.727 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.756 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 0.927 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 143 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 130 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 3.57 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 350 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 7570 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 2110 |
| 24 | REACTANCE (Ω/km) |  | 0.082 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner & outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  |  |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | TECHNICAL DESCRIPTION |  | 3×25+16 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWAT / PVC |
| 4 | INTERNAL CODE |  | 2116607016 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (CAT.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 25 (Phase) , 16 (Neutral) , Class 2 (IEC 60228) |
| 8 | NO.OF CORES |  | 3½ |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.9 (For Core 25) XLPE / 0.7 ( For Core 16) |
|  | CORE INSULATION COLORS |  | Red, Yellow, Blue, Black for neutral core |
| 10 | INNER SHEATH |  | Extruded PVC / 1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.21) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 27.5 |
| III. ELECTRICAL & MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°c (Ω/km) |  | 0.727 (For Core 25) 1.15 (For Core 16) |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.756 (For Core 25) 1.96 (For Core 16) |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90°c (Ω/km) |  | 0.927 (For Core 25) 1.47 (For Core 16) |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC(A) |  | 143 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 130 |
| 19 | 1 SEC. DURATION SHORT TIME RATING OF CORES (kA) |  | 3.58 (For Core 25) 2.29 (For Core 16) |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 330 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 6810 |
| 22 | MAX. CONDUCTOR TEMPERATURE: |  |  |
|  | AT CONTINUOUS RATING (°C) |  | 90 |
|  | AT SHORT CIRCUIT (°C) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 1950 |
| 24 | REACTANCE (Ω/km) |  | 0.082 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC outer sheath |  | SWAT: Steel wire armor + Open helix tape |  |
| PVC : Polyvinyl chloride |  |  |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | TECHNICAL DESCRIPTION |  | 3×35+16 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116607017 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (CAT.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 35 (Phase), 16 (Neutral), Class 2 (IEC 60228) |
| 8 | NO.OF CORES |  | 3½ |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.9 (For Core 35) XLPE / 0.7 (For Core 16) |
|  | CORE INSULATION COLORS |  | Red, Yellow, Blue, Black for neutral core |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.23.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.9 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 30.5 |
| III. ELECTRICAL & MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°c (Ω/km) |  | 0.524 (For Core 35) 1.15 (For Core 16) |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.545 (For Core 35) 1.96 (For Core 16) |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90°c (Ω/km) |  | 0.669 (For Core 35) 1.47 (For Core 16) |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC(A) |  | 173 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 160 |
| 19 | 1 SEC. DURATION SHORT TIME RATING OF CORES (kA) |  | 5 (For Core 35) 2.29 (For Core 16) |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 365 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 8375 |
| 22 | MAX. CONDUCTOR TEMPERATURE: |  |  |
|  | AT CONTINUOUS RATING (°C) |  | 90 |
|  | AT SHORT CIRCUIT (°C) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 2300 |
| 24 | REACTANCE (Ω/km) |  | 0.077 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner & outer sheath |  | SWA: Steel Wire Armor |  |
| PVC : Polyvinyl chloride |  |  |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | TECHNICAL DESCRIPTION |  | 3×50+25 SM/RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116704001 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 50 (Phase-Sector), 25 (Neutral-Circular), Class 2 (IEC 60228) |
| 8 | NO.OF CORES |  | 3½ |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 1 (For Core 50) XLPE / 0.9 (For Core 25) |
|  | CORE INSULATION COLORS |  | Red, Yellow, Blue, Black for neutral core |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.24.8) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 2 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 32 |
| III. ELECTRICAL & MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°c (Ω/km) |  | 0.387 (For Core 50) 0.727 (For Core 25) |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.402 (For Core 50) 0.756 (For Core 25) |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90°c (Ω/km) |  | 0.494 (For Core 50) 0.927 (For Core 25) |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC(A) |  | 205 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 195 |
| 19 | 1 SEC. DURATION SHORT TIME RATING OF CORES (kA) |  | 7.15 (For Core 50) 3.58 (For Core 25) |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 385 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 9215 |
| 22 | MAX. CONDUCTOR TEMPERATURE: |  |  |
|  | AT CONTINUOUS RATING (°C) |  | 90 |
|  | AT SHORT CIRCUIT (°C) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 2790 |
| 24 | REACTANCE (Ω/km) |  | 0.076 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | SM: Sector stranded conductor |  |
| Y: PVC inner & outer sheath |  | R: Round wire armor |  |
| PVC : Polyvinyl chloride |  | SWA: Steel wire armor |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | TECHNICAL DESCRIPTION |  | 3×70+35 SM/RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116704002 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (CAT.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 70 (Phase-Sector), 35 (Neutral-Circular), Class 2 (IEC 60228) |
| 8 | NO.OF CORES |  | 3½ |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 1.1 (For Core 70) XLPE / 0.9 (For Core 35) |
|  | CORE INSULATION COLORS |  | Red, Yellow, Blue, Black for neutral core |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 2 (Dia. under armor: Approx.27.8) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 2.1 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 36 |
| III. ELECTRICAL & MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°c (Ω/km) |  | 0.268 (For Core 70) 0.524 (For Core 35) |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.279 (For Core 70) 0.544 (For Core 35) |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90°c (Ω/km) |  | 0.342 (For Core 70) 0.669 (For Core 35) |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC(A) |  | 252 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 247 |
| 19 | 1 SEC. DURATION SHORT TIME RATING OF CORES (KA) |  | 10 (For Core 70) 5 (For Core 35) |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 430 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 11665 |
| 22 | MAX. CONDUCTOR TEMPERATURE: |  |  |
|  | AT CONTINUOUS RATING (°C) |  | 90 |
|  | AT SHORT CIRCUIT (°C) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 3790 |
| 24 | REACTANCE (Ω/km) |  | 0.075 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | SM: Stranded sector shaped copper conductor |  |
| Y: PVC inner & outer sheath |  | R: Round wire armor |  |
| PVC : Polyvinyl chloride |  | SWA: Steel Wire Armor |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | TECHNICAL DESCRIPTION |  | 1×300 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / AWA / PVC |
| 4 | INTERNAL CODE |  | 2116607001 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 300, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 1 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 1.8 |
|  | CORE INSULATION COLOR |  | Black |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of aluminum wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 2 (Dia. under armor: Approx.29) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 2.1 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 37 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 0.0601 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.0624 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 0.0802 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | Trefoil: 587 , Flat: 689 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | Trefoil: 697 , Flat: 864 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 42.93 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 555 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 12320 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 3655 |
| 24 | REACTANCE (Ω/km) |  | 0.088 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner & outer sheath |  | AWA: Aluminum Wire Armor |  |
| PVC : Polyvinyl chloride |  |  |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | TECHNICAL DESCRIPTION |  | 3×120+70 SM Fire Resistant |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XHRH |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / Mica Tape / XLPE / HFLS / SWA / HFLS |
| 4 | INTERNAL CODE |  | 2128002001 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502 , IEC 60228 , IEC 60332-3-24(Cat.C) , IEC 60331 |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Sector Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 120 (Phase), 70 (Neutral), Class 2 (IEC 60228) |
|  | FIRE RESISTANT TAPE |  | Mica tape as a fire resistant tape wrapped over each conductor with 100% coverage |
| 8 | NO.OF CORES |  | 3½ |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 1.2 (For Core 120) XLPE / 1.1 (For Core 70) |
|  | CORE INSULATION COLORS |  | Red, Yellow, Blue, Black for neutral core |
| 10 | INNER SHEATH |  | Extruded HFLS / 1.3 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 2.5 (Dia. under armor: Approx.37.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | HFLS (Flame Retardant) / 2.5 |
|  | OUTER SHEATH COLOR |  | Red |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 47.5 |
| III. ELECTRICAL & MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°c (Ω/Km) |  | 0.153 (For Core 120) 0.268 (For Core 70) |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.159 (For Core 120) 0.279 (For Core 70) |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90°c (Ω/Km) |  | 0.196 (For Core 120) 0.342 (For Core 70) |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC(A) |  | 346 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 355 |
| 19 | 1 SEC. DURATION SHORT TIME RATING OF CORES (KA) |  | 17.17 (For Core 120) 10 (For Core 70) |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 570 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 19880 |
| 22 | MAX. CONDUCTOR TEMPERATURE: |  |  |
|  | AT CONTINUOUS RATING (°C) |  | 90 |
|  | AT SHORT CIRCUIT (°C) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 6640 |
| 24 | REACTANCE (Ω/km) |  | 0.072 |
| Notes: |  |  |  |
| SM: Sector stranded conductor |  | R: Round wire armor |  |
| H: HFLS Bedding , outer sheath |  | SWA: Steel wire armor |  |
| HFLS : Halogen free and low smoke material |  |  |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 2×4 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116616017 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 4, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 2 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Blue, Black |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 2.6 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead / 1.2 (Dia. Over Lead: Approx.16) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.18) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC ( Flame Retardant ) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 24.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 4.61 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 4.79 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 5.88 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 62 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 51 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 0.572 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 295 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 5400 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 1670 |
| 24 | REACTANCE (Ω/km) |  | 0.099 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC bedding and outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 2×16 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116616018 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 16, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 2 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Blue, Black |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead / 1.2 (Dia. Over Lead: Approx.17.5) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx. 19.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 26 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/Km) |  | 1.15 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 1.20 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 1.47 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 122 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 115 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (KA) |  | 2.29 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 315 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 6085 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 2080 |
| 24 | REACTANCE (Ω/km) |  | 0.088 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC bedding and outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×4 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY-J |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116618003 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 4, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Blue, Black, Yellow with green strip |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 2.3 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead / 1.2 (Dia. Over Lead: Approx.16) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.18) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 24.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 4.61 |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 4.79 |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 5.88 |
| 19 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 52 |
| 20 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 42 |
| 21 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 0.57 |
| 22 | MINIMUM BENDING RADIUS (mm) |  | 295 |
| 23 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 5400 |
| 24 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 26 | APPROX. CABLE WEIGHT (kg/km) |  | 1690 |
| 27 | REACTANCE (Ω/km) |  | 0.088 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner or outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  | -J : With protective earth core |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×2.5 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY-J |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116601001 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 2.5, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Blue, Black, Yellow with green strip |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 0.9 (Dia. under armor: Approx.10) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 15 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 7.41 |
| 18 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 7.70 |
| 19 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 9.45 |
| 20 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 40 |
| 21 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 32 |
| 22 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 0.358 |
| 23 | MINIMUM BENDING RADIUS (mm) |  | 180 |
|  | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 2025 |
| 24 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 17 | APPROX. CABLE WEIGHT (kg/km) |  | 435 |
| 18 | REACTANCE (Ω/km) |  | 0.101 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner & outer sheath |  | SWA: Steel Wire Armor |  |
| PVC : Polyvinyl chloride |  | -J: With protective earth core |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×4 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY-J |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116601002 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 4, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Blue, Black, Yellow with green strip |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.25 (Dia. under armor: Approx.11) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 17 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 4.61 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 4.80 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 5.88 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 52 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 42 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 0.572 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 205 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 2600 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 610 |
| 24 | REACTANCE (Ω/km) |  | 0.099 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner & outer sheath |  | SWA: Steel Wire Armor |  |
| PVC : Polyvinyl chloride |  | -J: With protective earth core |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×6 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY-J |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116601041 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 6, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Blue, Black, Yellow with green strip |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.25 (Dia. under armor: Approx.12) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 18 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 3.08 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 3.20 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 3.93 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 64 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 53 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 0.858 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 220 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 2920 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 710 |
| 24 | REACTANCE (Ω/km) |  | 0.094 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner & outer sheath |  | SWA: Steel Wire Armor |  |
| PVC : Polyvinyl chloride |  | -J : With protective earth core |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×10 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY-J |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116601003 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (CAT.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 10, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Blue, Black, Yellow with green strip |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.25 (Dia. under armor: Approx.14) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant ) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 20 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 1.83 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 1.90 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 2.33 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 86 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 73 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 1.43 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 240 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 3600 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 920 |
| 24 | REACTANCE (Ω/km) |  | 0.093 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | -J : With protective earth core |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×50 SM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY-J |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116801007 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (CAT.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Sector Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 50, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 1 |
|  | CORE INSULATION COLOR |  | Blue, Black, Yellow with green strip |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.22) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.9 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 29 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/Km) |  | 0.387 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.402 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 0.494 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 205 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 195 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (KA) |  | 7.15 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 350 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 7570 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 2425 |
| 24 | REACTANCE (Ω/km) |  | 0.076 |
| Notes: |  |  |  |
| SM: Sector shaped stranded conductor |  | R: Round wire armor |  |
| Y: PVC outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | -J : With protective earth core |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 2×6 Flexible Cable |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2118114001 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (CAT.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Flexible annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 6, Class 5 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 2 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Red, Black |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.25 (Dia. under armor: Approx.11.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 17.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 3.30 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 3.43 |
| 16 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 71 |
| 17 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 63 |
| 18 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 0.858 |
| 19 | MINIMUM BENDING RADIUS (mm) |  | 175 |
| 20 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 2760 |
| 21 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 22 | APPROX. CABLE WEIGHT (kg/km) |  | 630 |
| 23 | REACTANCE (Ω/km) |  | 0.094 |
| Notes: |  |  |  |
| Y: PVC inner & outer sheath |  | R: Round wire armor |  |
| PVC : Polyvinyl chloride |  | SWA: Steel Wire Armor |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 2×50 Flexible Cable |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2118114002 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (CAT.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Flexible annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 50, Class 5 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 2 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 1 |
|  | CORE INSULATION COLOR |  | Red, Black |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.25) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 2 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 32 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 0.386 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.401 |
| 16 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 246 |
| 17 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 214 |
| 18 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 7.15 |
| 19 | MINIMUM BENDING RADIUS (mm) |  | 320 |
| 20 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 9215 |
| 21 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 22 | APPROX. CABLE WEIGHT (kg/km) |  | 2370 |
| 23 | REACTANCE (Ω/km) |  | 0.076 |
| Notes: |  |  |  |
| Y: PVC inner & outer sheath |  | R: Round wire armor |  |
| PVC : Polyvinyl chloride |  | SWA: Steel Wire Armor |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 2×95 Flexible Cable |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2118114003 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (CAT.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Flexible annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 95, Class 5 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 2 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 1.1 |
|  | CORE INSULATION COLOR |  | Red, Black |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 2 (Dia. under armor: Approx.32.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 2.3 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 41 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 0.206 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.214 |
| 16 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 333 |
| 17 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 335 |
| 18 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 13.6 |
| 19 | MINIMUM BENDING RADIUS (mm) |  | 410 |
| 20 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 15130 |
| 21 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 22 | APPROX. CABLE WEIGHT (kg/km) |  | 3990 |
| 23 | REACTANCE (Ω/km) |  | 0.074 |
| Notes: |  |  |  |
| Y: PVC inner & outer sheath |  | R: Round wire armor |  |
| PVC : Polyvinyl chloride |  | SWA: Steel Wire Armor |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 2×120 Flexible Cable |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2118114004 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (CAT.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Flexible annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 120, Class 5 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 2 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 1.2 |
|  | CORE INSULATION COLOR |  | Red, Black |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.3 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 2.5 (Dia. under armor: Approx.36.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 2.4 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 46 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 0.161 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.167 |
| 16 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 374 |
| 17 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 390 |
| 18 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 17.2 |
| 19 | MINIMUM BENDING RADIUS (mm) |  | 460 |
| 20 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 19045 |
| 21 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 22 | APPROX. CABLE WEIGHT (kg/km) |  | 5200 |
| 23 | REACTANCE (Ω/km) |  | 0.072 |
| Notes: |  |  |  |
| Y: PVC inner & outer sheath |  | R: Round wire armor |  |
| PVC : Polyvinyl chloride |  | SWA: Steel Wire Armor |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 2×150 Flexible Cable |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2118114005 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (CAT.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Flexible annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 150, Class 5 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 2 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 1.4 |
|  | CORE INSULATION COLOR |  | Red, Black |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.3 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 2.5 (Dia. under armor: Approx.40.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 2.6 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 50.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 0.129 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.134 |
| 16 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 430 |
| 17 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 448 |
| 18 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 21.4 |
| 19 | MINIMUM BENDING RADIUS (mm) |  | 505 |
| 20 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 22955 |
| 21 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 22 | APPROX. CABLE WEIGHT (kg/km) |  | 6160 |
| 23 | REACTANCE (Ω/km) |  | 0.073 |
| Notes: |  |  |  |
| Y: PVC inner & outer sheath |  | R: Round wire armor |  |
| PVC : Polyvinyl chloride |  | SWA: Steel Wire Armor |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 2×185 Flexible Cable |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2118114006 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (CAT.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Flexible annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 185, Class 5 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 2 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 1.6 |
|  | CORE INSULATION COLOR |  | Red, Black |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.4 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 2.5 (Dia. under armor: Approx.45) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 2.7 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 55 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 0.106 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 0.110 |
| 16 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 485 |
| 17 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 516 |
| 18 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 26.5 |
| 19 | MINIMUM BENDING RADIUS (mm) |  | 550 |
| 20 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 26700 (Acc. to IEEE) |
| 21 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 22 | APPROX. CABLE WEIGHT (kg/km) |  | 7250 |
| 23 | REACTANCE (Ω/km) |  | 0.073 |
| Notes: |  |  |  |
| Y: PVC inner & outer sheath |  | R: Round wire armor |  |
| PVC : Polyvinyl chloride |  | SWA: Steel Wire Armor |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×4 RM Control Cable |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | NYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116925001 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 4, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | PVC / 1 |
|  | CORE INSULATION COLOR |  | Black and sequentially white numbered |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.7 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead /1.2 (Dia. Over Lead: Approx.16) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.18) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 24.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 4.61 |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 4.79 |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 70ºC (Ω/km) |  | 5.52 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 0.46 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 295 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 5315 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 70 |
|  | AT SHORT CIRCUIT (ºC) |  | 160 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 1715 |
| 24 | REACTANCE (Ω/km) |  | 0.099 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | K: Lead sheath |  |
| Y: PVC Insulation , bedding and outer sheath |  | LC: Lead Covering |  |
| PVC : Polyvinyl chloride |  |  |  |
| R: Round wire armor |  |  |  |
| SWA: Steel wire armor |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×6 RM Control Cable |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | NYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116925002 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 6, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | PVC / 1 |
|  | CORE INSULATION COLOR |  | Black and sequentially white numbered |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.5 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead / 1.2 (Dia. Over Lead: Approx.16) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.18) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 24.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 3.08 |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 3.20 |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 70ºC (Ω/km) |  | 3.69 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 0.690 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 295 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 5405 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 70 |
|  | AT SHORT CIRCUIT (ºC) |  | 160 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 1745 |
| 24 | REACTANCE (Ω/km) |  | 0.094 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | K: Lead sheath |  |
| Y: PVC Insulation , bedding and outer sheath |  | LC: Lead Covering |  |
| PVC : Polyvinyl chloride |  |  |  |
| R: Round wire armor |  |  |  |
| SWA: Steel wire armor |  |  |  |

| ITEM NO. | TECHNICAL DESCRIPTION |  | ## 7×2.5 RM Control Cable |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | NYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116925003 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 2.5, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 7 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | PVC / 0.8 |
|  | CORE INSULATION COLOR |  | Black and sequentially white numbered |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.1 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead / 1.2 (Dia. Over Lead: Approx.16) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of round galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.18) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 24.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 7.41 |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 7.70 |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 70ºC (Ω/km) |  | 8.87 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 0.29 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 295 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 5400 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 70 |
|  | AT SHORT CIRCUIT (ºC) |  | 160 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 1705 |
| 24 | REACTANCE (Ω/km) |  | 0.101 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC insulation & Bedding or outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| LC: Lead Covering |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 10×2.5 RM Control Cable |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | NYKYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116925004 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 2.5, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 10 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | PVC / 0.8 |
|  | CORE INSULATION COLOR |  | Black and sequentially white numbered |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead /1.2 (Dia. Over Lead: Approx.19.5) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.21.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.9 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 28.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 7.41 |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 7.70 |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 70ºC (Ω/km) |  | 8.87 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 0.29 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 340 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 7310 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 70 |
|  | AT SHORT CIRCUIT (ºC) |  | 160 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 2245 |
| 24 | REACTANCE (Ω/km) |  | 0.101 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | K: Lead sheath |  |
| Y: PVC Insulation , bedding and outer sheath |  | LC: Lead Covering |  |
| PVC : Polyvinyl chloride |  |  |  |
| R: Round wire armor |  |  |  |
| SWA: Steel wire armor |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×4 RM Control Cable |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | NYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116902014 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 4, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | PVC / 1 |
|  | CORE INSULATION COLOR |  | Black and sequentially white numbered |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.25 (Dia. under armor: Approx.12.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 18.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/Km) |  | 4.61 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 4.79 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 70ºC (Ω/km) |  | 5.52 |
| 17 | 1 SEC DURATION SHORT TIME RATING OF CORES (KA) |  | 0.46 |
| 18 | MINIMUM BENDING RADIUS (mm) |  | 225 |
| 19 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 600 |
| 20 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 70 |
|  | AT SHORT CIRCUIT (ºC) |  | 160 |
| 21 | APPROX. CABLE WEIGHT (kg/km) |  | 680 |
| 22 | REACTANCE (Ω/km) |  | 0.099 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC insulation or outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 7×2.5 RM Control Cable |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | NYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116902001 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 2.5, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 7 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | PVC / 0.8 |
|  | CORE INSULATION COLOR |  | Black and sequentially white numbered |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.25 (Dia. under armor: Approx.13.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 19.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 7.41 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 7.70 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 70ºC (Ω/km) |  | 8.87 |
| 17 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 0.288 |
| 18 | MINIMUM BENDING RADIUS (mm) |  | 235 |
| 19 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 3425 |
| 20 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 70 |
|  | AT SHORT CIRCUIT (ºC) |  | 160 |
| 21 | APPROX. CABLE WEIGHT (kg/km) |  | 760 |
| 22 | REACTANCE (Ω/km) |  | 0.101 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC insulation or outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 12×2.5 RM Control Cable |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | NYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116902002 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 2.5, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 12 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | PVC / 0.8 |
|  | CORE INSULATION COLOR |  | Black and sequentially white numbered |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.18) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 24.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/Km) |  | 7.41 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 7.70 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 70ºC (Ω/km) |  | 8.87 |
| 17 | 1 SEC DURATION SHORT TIME RATING OF CORES (KA) |  | 0.29 |
| 18 | MINIMUM BENDING RADIUS (mm) |  | 295 |
| 19 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 5400 |
| 20 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 70 |
|  | AT SHORT CIRCUIT (ºC) |  | 160 |
| 21 | APPROX. CABLE WEIGHT (kg/km) |  | 1205 |
| 22 | REACTANCE (Ω/km) |  | 0.101 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC insulation or outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  |  |  |

| ITEM NO. | TECHNICAL DESCRIPTION |  | 16×2.5 RM Control Cable |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | NYRY |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116902015 |
| 5 | CABLE RATED VOLTAGE U0 / U (kV ) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 2.5, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 16 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | PVC / 0.8 |
|  | CORE INSULATION COLORS |  | Black and sequentially white numbered |
| 10 | BEDDING MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 11 | ARMOR TYPE |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.19.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 26 |
| III. ELECTRICAL & MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 7.41 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 7.70 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 70°C (Ω/km) |  | 8.87 |
| 17 | 1 SEC. DURATION SHORT TIME RATING OF CORES (KA) |  | 0.288 |
| 18 | MINIMUM BENDING RADIUS (mm) |  | 315 |
| 19 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 6085 |
| 20 | MAX. CONDUCTOR TEMPERATURE: |  |  |
|  | AT CONTINUOUS RATING (°C) |  | 70 |
|  | AT SHORT CIRCUIT (°C) |  | 160 |
| 21 | APPROX. CABLE WEIGHT (kg/km) |  | 1435 |
| 22 | REACTANCE (Ω/km) |  | 0.101 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC insulation or outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  |  |  |

| ITEM NO. | TECHNICAL DESCRIPTION |  | ## 3×6 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY-J |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116618005 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 6, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Blue, Black, Yellow with green strip |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.7 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead / 1.2 (Dia. Over Lead: Approx.17.5) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.19.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 24.5 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/Km) |  | 3.08 |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 3.20 |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 3.93 |
| 19 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 64 |
| 20 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 53 |
| 21 | 1 SEC DURATION SHORT TIME RATING OF CORES (KA) |  | 0.86 |
| 22 | MINIMUM BENDING RADIUS (mm) |  | 295 |
| 23 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 5405 |
| 24 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 26 | APPROX. CABLE WEIGHT (kg/km) |  | 1725 |
| 27 | REACTANCE (Ω/km) |  | 0.094 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  | -J: With protective earth core |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 5×10 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYKYRY-J |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / LC / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116618006 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 10, Class 2 (According to IEC 60228) |
| 8 | NO.OF CORES |  | 5 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue, Black, Yellow with green strip |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1 |
| 11 | METALLIC SCREEN MATERIAL / THICKNESS (-/mm) |  | Lead / 1.2 (Dia. Over Lead: Approx.19.5) |
| 12 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1 |
| 13 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.21.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 14 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 15 | APPROX. OVERALL DIAMETER (mm) |  | 28 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 16 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 1.83 |
| 17 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 1.90 |
| 18 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 2.33 |
| 19 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 85 |
| 20 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 72 |
| 21 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 1.43 |
| 22 | MINIMUM BENDING RADIUS (mm) |  | 340 |
| 23 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 7055 |
| 24 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 26 | APPROX. CABLE WEIGHT (kg/km) |  | 2405 |
| 27 | REACTANCE (Ω/km) |  | 0.093 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC bedding and outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | K: Lead sheath |  |
| 2X: XLPE insulation |  | LC: Lead Covering |  |
| XLPE : Cross linked polyethylene |  | -J : With protective earth core |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×2.5 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY-J |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116601001 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 2.5, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Blue, Black, Yellow with green strip |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 0.9 (Dia. under armor: Approx.10) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 15 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 7.41 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 7.70 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 9.45 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 40 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 32 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 0.358 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 180 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 2025 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 435 |
| 24 | REACTANCE (Ω/km) |  | 0.101 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner & outer sheath |  | SWA: Steel Wire Armor |  |
| PVC : Polyvinyl chloride |  | -J: With protective earth core |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 3×6 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY-J |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116601041 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 6, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 3 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Blue, Black, Yellow with green strip |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC /1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.25 (Dia. under armor: Approx.12) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 18 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 3.08 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 3.20 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 3.93 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 64 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 53 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 0.858 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 220 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 2920 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 710 |
| 24 | REACTANCE (Ω/km) |  | 0.094 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC inner & outer sheath |  | SWA: Steel Wire Armor |  |
| PVC : Polyvinyl chloride |  | -J : With protective earth core |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

| ITEM NO. | ## TECHNICAL DESCRIPTION |  | ## 5×10 RM |
| --- | --- | --- | --- |
| I. GENERAL |  |  |  |
| 1 | CABLE TYPE |  | N2XYRY-J |
| 2 | MANUFACTURER’S NAME |  | SIMCO |
| 3 | ABBREVIATED DESCRIPTION |  | Cu / XLPE / PVC / SWA / PVC |
| 4 | INTERNAL CODE |  | 2116601014 |
| 5 | RATED VOLTAGE (U0/U) (kV) |  | 0.6 / 1 |
| 6 | STANDARD |  | IEC 60502, IEC 60228, IEC 60332-3-24 (Cat.C) |
| II. CONSTRUCTION |  |  |  |
| 7 | CONDUCTOR MATERIAL & CONSTRUCTION |  | Stranded annealed copper |
|  | CONDUCTOR CROSS_SECTION (mm²) |  | 10, Class 2 (according to IEC 60228) |
| 8 | NO.OF CORES |  | 5 |
| 9 | CORE INSULATION MATERIAL / THICKNESS (-/mm) |  | XLPE / 0.7 |
|  | CORE INSULATION COLOR |  | Red, Yellow, Blue, Black, Yellow with green strip |
| 10 | INNER SHEATH MATERIAL / THICKNESS (-/mm) |  | Extruded PVC / 1.2 |
| 11 | ARMOR TYPE AND MATERIAL |  | One layer of galvanized steel wires |
|  | DIAMETER OF ARMOR WIRES (mm) |  | 1.60 (Dia. under armor: Approx.17.5) |
|  | COVERAGE PERCENT OF ARMOR WIRES |  | >95% |
| 12 | OUTER SHEATH MATERIAL / THICKNESS (-/mm) |  | PVC (Flame Retardant) / 1.8 |
|  | OUTER SHEATH COLOR |  | Black |
| 13 | APPROX. OVERALL DIAMETER (mm) |  | 24 |
| III. ELECTRICAL AND MECHANICAL CHARACTERISTICS |  |  |  |
| 14 | MAX. DC RESISTANCE OF CONDUCTOR AT 20°C (Ω/km) |  | 1.83 |
| 15 | MAX. DC RESISTANCE OF CONDUCTOR AT 30°C (Ω/km) |  | 1.90 |
| 16 | MAX. AC RESISTANCE OF CONDUCTOR AT 90ºC (Ω/km) |  | 2.33 |
| 17 | CURRENT CARRYING CAPACITY IN GROUND AT 20ºC (A) |  | 85 |
| 18 | CURRENT CARRYING CAPACITY IN AIR AT 30ºC (A) |  | 72 |
| 19 | 1 SEC DURATION SHORT TIME RATING OF CORES (kA) |  | 1.43 |
| 20 | MINIMUM BENDING RADIUS (mm) |  | 290 |
| 21 | MAXIMUM PULLING STRESS/PER CABLE (N) |  | 5185 |
| 22 | MAX. CONDUCTOR TEMPERATURE |  |  |
|  | AT CONTINUOUS RATING (ºC) |  | 90 |
|  | AT SHORT CIRCUIT (ºC) |  | 250 |
| 23 | APPROX. CABLE WEIGHT (kg/km) |  | 1350 |
| 24 | REACTANCE (Ω/km) |  | 0.093 |
| Notes: |  |  |  |
| RM: Circular stranded conductor |  | R: Round wire armor |  |
| Y: PVC outer sheath |  | SWA: Steel wire armor |  |
| PVC : Polyvinyl chloride |  | -J : With protective earth core |  |
| 2X: XLPE insulation |  |  |  |
| XLPE : Cross linked polyethylene |  |  |  |

Sample Marking:

- IEC 60502 3×95 RM/16 mm2 N2XSEYKYRY 6/10/(12) KV POWER CABLE S.W.A (Order No) SIMCO 1403 MADE IN IRAN (Length) - IEC 60502 3×4 RM mm2 N2XYRY 0.6/1KV POWER CABLE S.W.A (Order No.) SIMCO 1403 MADE IN IRAN (Length) - IEC 60502 6×2.5 RM mm2 NYRY 0.6/1KV CONTROL CABLE S.W.A (Order No.) SIMCO 1403 MADE IN IRAN (Length)