## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0022 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2637 |  |  | Transmital Date: 3/12/2024
Document Title: P&ID - Fuel Gas System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-2637 |  |  | Transmital Date: 3/12/2024
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-PR-PI-0022_D08 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با اعمال نظرات ذیل، مدرک مورد تایید می باشد. شایان ذکر است که مطابق شرایط عمومی پیمان فی ما بین و با توجه به مسئولیتهای مالی-قراردادی پیمانکار، مسئولیت بروز هرگونه اشتباه و تناقض، کمبود اسناد و مدارک فنی و اطلاعات تهیه شده از سوی پیمانکار اعم از اینکه از سوی کارفرما تایید شده و یا نشده باشد بر عهده پیمانکار است. |  | BK-SUR-ENG-PCS-03-09183 | 2024-03-30 | مورد تایید می باشد.
2 | دلیل بالا بودن سایز خروجی(4”) نسبت به سایز ورودی(3") در Fuel Gas Drum چیست؟ |  | BK-SUR-ENG-PCS-03-09183 | 2024-03-30 | سایز 4 " به علت وجود تجهیزات اندازه گیری خوردگی بر روی این خط در نظر گرفته شده است.
3 | پیشنهاد می شود برای PDG مربوط به Demister تجهیز Fuel Gas Drum یک آلارم High لحاظ گردد. |  | BK-SUR-ENG-PCS-03-09183 | 2024-03-30 | مورد تایید می باشد.
4 | .ضروريست نقطه نظرات ذينفع اصلي در خصوص اين مدرك اعمال گردد |  | BK-SUR-ENG-PCS-03-09183 | 2024-03-30 | مورد تایید می باشد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: