## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-TB-0001-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2470 |  |  | Transmital Date: 07-Nov-2023
Document Title: TBE For Transformers |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0208-EL-TR-2470 |  |  | Transmital Date: 07-Nov-2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-TB-0001-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 |  |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18
2 | Latest revision of project documents such as data sheet shall be completed by vendor and submitted again. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | Confirmed
3 | Following items shall be added to TCL and shall be clarified by vendors: |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18
3-1 | MR and all attached documents of MR shall be read, signed and stamped by Vendor. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | Confirmed
3-2 | Vendor shall submitted temperature de‐rating factors of equipment. It means Vendor shall de-rate the rated current of equipment on the site condition such way that de-rated current be equal or higher than rated current. De-rating curves/Tables (altitude & Ambient Temperature) shall be submitted at this stage. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | Confirmed. Derating curves will be submitted after P.O
3-3 | Certificate or license, Test reports and type test shall be submitted based on latest revision of IEC 60076. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | Sample type tests had been submitted
3-4 | Added to item 12, Vendor List: Sub vendor list shall be submitted and following items shall be specified in sub vendor list: -Manufacture -Country of origin -Model |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | Sub vendor list is attached
3-5 | As built documents and drawings are in vendor scope of work. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | Confirmed
3-6 | Native completed deviation from Purchase Order or Purchaser procurement documents shall be submitted in next revision. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | Submitted
3-7 | All electrical equipment which is not in MOP and project AVL is not accepted after P.O. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | Our sub vendor list is submitted please review it.
3-8 | Catalogue of all equipment such as transformer, CT, etc. shall be submitted by Vendor. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | Submitted
3-9 | Preliminary ITP shall be submitted at this stage and will be finalized in the PIM meeting. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | Submitted
4 | Conclusion column in devotion list shall be completed by consultant. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18
5 | All rows in TBE that has been mentioned "Clarification is Required", shall be approved by vendor otherwise it shall be mentioned in deviation list and shall be clarified. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | Submitted
6 |  |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18
7 | As per latest project document (data sheet and SLD) one CT is required on 800kVA transformer neutral point. But in the clarifications it has been deleted. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18
8 | Complementary comments will be submitted after receiving revised document. |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18
9 | Following items to be added to TBE: 1- Commissioning Spare part 2- Two years Spare part 3- Reference list 4- Guarantee 5- Preliminary ITP 6- Packing and transportation 7- Delivery point 8- Deviation List |  | BK-SUR-ENG-ELE-02-08779 | 2023-11-18 | 1- Confirmed 2- Confirmed 3- Confirmed 4- Acc. To commercial offer 5- Confirmed 6- Packing Procedure is submitted 7- Acc. To commercial offer 8- Confirmed
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 18-Nov-2023 |  |  |  |  | Date: