| # | Clarification Title | Clarification Description (Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.02) | Conclusion (Rev.02) (VENDOR to Confirm & Consider in the Final Offers) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ELECTRICAL |  |  |  |  |  |  |  |
|  | Design Criteria | Vendor To confirm That All supplied material all in full compliance with Project site condition : - Min/Max air temperature = 0°C / 52°C - Relative humidity = 100% max at 52°C - Altitude = 12 m a.s.l. - Climate = Class 4 (Very High) | confirmed |  |  |  |  |  |
|  | Documents Priority | All The equipment’s shall be engineered, designed, manufactured, tested and installed in accordance with the following standards: - Local Codes & Standards - Iranian Petroleum Standard (IPS) - International Codes & Standards - IEC (International Electro technical Commission) - BS (British Standard) - IEEE (Institute of Electrical and Electronics Engineers) - API (American Petroleum Institute) Any conflict between Project Documents, contract documents, standards and codes of practice shall be referred to the Customer for clarification. Where conflict occur, the order of precedence shall be as follows 1-Contract Scope of Work including this TCL. 2-Project Reference Documents. 3-Applicable International Codes and Standards. | confirmed |  |  |  |  |  |
|  | Scope of Supply | Minimum Scope of work and supply are in full compliance with Project MR (BK-GCS-PEDCO-120-EL-MR-0001). It has been Listed but not Limited to the following Items: - Full Engineering Services. - Two sets 11/0.42 KV, Hermetically Sealed (1250KVA - One set 11/3.45 KV, Hermetically Sealed (800KVA) - Inspection & Test ACC to ITP/QCP - Site Supervisory Servicers (Optional) | 1- Acc to contract 2-Ok 3-Ok 4- Acc to ITP of IRAN TRANSFO 5- Acc to contract |  |  |  |  |  |
|  | Deviation List | Technical requirements shall be according to project specification in as minimum except those clearly specified in “deviation form”. BK-GNRAL-PEDCO-000-EL-DC-0001 (Electrical System Design Criteria) BK-GNRAL-PEDCO-000-EL-SP-0004 (Specification for Transformers) | Deviation list is attached. |  |  |  |  |  |
|  | General | Vendor shall inform the purchaser of any deviations/Exceptions from all Technical Documents attached to the MR, TCL and codes & standards referred in the documents by issuing a New Deviation/Exception List With the respect to latest Modification and revised technical offer for purchaser's review and approval. Otherwise, the vendor must declare full compliance between all documents attached to the Inquiry package. | Deviation list is attached. |  |  |  |  |  |
|  | General | Project Datasheet & TBE Table Shall be fill Out and return to purchaser. | Datasheet is attached. TBE is not found. |  |  |  |  |  |
|  | Scope of Supply | Transformer 800 KVA is 11/3.45 KV. This item will be revised in next revision of data sheet. | Confirmed |  |  |  |  |  |
|  | Cables for 1250KVA transformer | - 11 kV Cables Size & Number: 1x3x95 (CU/SM/XLPE/SM/SC/PVC/SWA/PVC) - 0.42 kV Cable Size & Number 14x(1x300), (CU/XLPE/Bd/AWA/PVC) - Type & Size of Power Cable Glands Primary: M90 Secondary: M40 - Type & Size of Cable Glands (Control Cable) 12x2.5, (CU/PVC/SWA/PVC), M25 - Undrilled Non Magnetic Gland Plated shall be provided. | Confirmed (Gland: by customer) Gland plate would be provided for HV and LV cable boxes. It should be noted that cable entry is considered from bottom for both sides. |  |  |  |  |  |
|  | Cables for 800KVA transformer | - 11 kV Cables Size & Number: 1x3x95 (CU/SM/XLPE/SM/SC/PVC/SWA/PVC) - 3.45 kV Cable Size & Number 1x3x95 (CU/SM/XLPE/SM/SC/PVC/SWA/PVC) - Type & Size of Power Cable Glands Primary: M90 Secondary: M75 - Type & Size of Cable Glands (Control Cable) 12x2.5, (CU/PVC/SWA/PVC), M25 - Undrilled Non Magnetic Gland Plated shall be provided. | Confirmed (Gland: by customer) gland plate would be provided for HV and LV cable boxes. It should be noted that cable entry is considered from bottom for both sides. |  |  |  |  |  |
|  | CT for Transformers | - Below CTs shall be Considered by Vendor on 1250 KVA Transformer: 2000/1A, 5P10 ,10VA - Below CTs shall be Considered by Vendor on 800 KVA Transformer: 630/1A, 5P10 ,10VA *Note: It is Preliminary and will be final by Switchgear Manufacturer. | Confirmed |  |  |  |  |  |
|  | Power Cable Gland | All Required Power Cable Glands & Plugs are in purchaser Scope of work and is ISO metric threaded in accordance with IEC60423. It should be Noted that Gland for Power Cables will be supplied by purchaser. | Gland plate would be provided. (Glands: By customer) |  |  |  |  |  |
|  | Vendor List | Vendor list & sub vendor list of manufacture shall be according to project AVL. Sub-vendor List for Electrical Equipment shall be submitted for review and approval in bid stage. | Sub vendor list is attached. |  |  |  |  |  |
|  | Spare Part | Spare Part for Commissioning and 2 Years Operation shall be Covered all requirement in Project Specification. | Attached. |  |  |  |  |  |
|  | Special Tools | Any Special Tools for Life time Operation shall be included in technical offer. | N.A. |  |  |  |  |  |
|  | Specification | Vendor shall submit the reference and experience list (as a separate file) for design & manufacturing of power transformer. | Reference list is attached. |  |  |  |  |  |
|  | Shipment | Vendor shall confirm that Packing, Marking, Preservation and Preparation for Shipment will be done in accordance to project specification. | Acc to IRAN TRANSFO Procedure |  |  |  |  |  |
|  | Arrangement | Transformer Outline Drawing shall be completed and LV/MV boxes shall be shown in top view for arrangement in shelter. | Outline drawing is revised. |  |  |  |  |  |
|  | Comments on deviation list | According to IPS-M-EL-1152 (2), The cover of the tank for sealed type transformer shall be welded to the tank with a continuous weld. Please follow it. | Bolted cover is desirable. welded cover is not suggested due to maintenance issues. |  |  |  |  |  |
|  | Comments on outline drawing | The location of HV & LV side of bushing will be finalized later. Please confirm that if is possible to change it in detail design? | Confirmed. |  |  |  |  |  |
|  | Comments on outline drawing | In items 7.16 to 7.20 of data sheet cables of transformers have been specified. In the cable boxes, when more than one conductor are to be connected, sufficient copper bars shall be provided to be connected to the cables indicated in data sheet. It shall be possible to test the cables without damaging the cables or the termination points of the transformer. Vendor shall consider all requirement for installation. The busbar for each phase (on LV busing) shall be such as cables 1*300 to be connected correctly. Please consider on outline drawing. | Busbar is considered for LV side of 1250 kVA transformer. |  |  |  |  |  |
|  | Temperature de‐Rating Factors | Vendor shall submitted temperature de‐rating factors of equipment. It means Vendor shall de-rate the rated current of equipment on the site condition such way that de-rated current be equal or higher than rated current. De-rating curves/Tables (altitude & Ambient Temperature) shall be submitted at this stage. | Confirmed |  |  |  |  |  |
|  | ITP & Test Report | Certificate or license, Test reports and type test shall be submitted based on latest revision of IEC 60076. | Confirmed. Has been attached |  |  |  |  |  |
|  | As Built | As built documents and drawings are in vendor scope of work. | Confirmed |  |  |  |  |  |