## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0007 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1961 |  |  | Transmital Date: 3/13/2023
Document Title: Calculation Note For Diesel Generator Sizing |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-1961 |  |  | Transmital Date: 3/13/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-CN-0007_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | توان 140 کیلووات در نظر گرفته شده برای سیستم HVAC زیاد می باشد، و لازم است که بررسی و اصلاح گردد. همچنین با توجه به احتمال ادغام ساختمان کنترل جدید در ساختمان موجود، در صورت حذف ساختمان کنترل جدید می بایست نسبت به به روزرسانی محاسبات دیزل اقدام گردد. |  | 1402-2294-9950 | 1402/01/15 | مدرک بر اساس آخرین لیست بار الکتریکی به شماره ترنسمیتال 2764 به روزرسانی گردید. همچنین با توجه به ادغام ساختمان کنترل جدید و موجود، توان در نظر گرفته شده سیستم HVAC به صورت یکپارچه و با توان 97.9 کیلووات می باشد.
2 | لازم است بر اساس آخرین ویرایش لیست بار الکتریکال تأیید شده مجددا به روزرسانی گردد. |  | 1402-2294-9950 | 1402/01/15
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: