## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0007 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1961 |  |  | Transmital Date: 3/13/2023
Document Title: Calculation Note For Diesel Generator Sizing |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-1961 |  |  | Transmital Date: 3/13/2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-CN-0007_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised base on comments on load list and shall be submitted as IFA after finalizing or minor comments on load list. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | در صورت وجود هر گونه تغییر احتمالی در ایست بار، این مدرک به روزرسانی خواهد شد. |  |  | Noted and Closed.
2 | Emergency loads table shall be added to this document as separated sheet base on load list. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | لیست بارها بر روی باسبار اضطراری اضافه گردیده است. |  |  | Noted and Closed.
3 | Total power of AC&DC UPS In the emergency loads table shall be considered for diesel sizing. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | مطابق با لیست بار، بارهای بر روی UPS و DC Charger به صورت Continuous بر روی دیزل ژنراتور قرار داده شده است. |  |  | Noted and Closed.
4 | It shall be clarify where the biggest motor starting power has been considered in diesel sizing on page 7, section 4.2. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | محاسبات بر اساس آخرین لیست بار به روزرسانی گردیده است. |  |  | Noted and Closed.
5 | It shall be clarify why temperature derating factor has been considered again in diesel sizing on page 7, section 4.4. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | محاسبات بر اساس آخرین لیست بار به روزرسانی گردیده است. |  |  | Noted and Closed.
6 | Editing error shall be modified on page 8, section 5.1. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | محاسبات بر اساس آخرین لیست بار به روزرسانی گردیده است. |  |  | Noted and Closed.
7 | As per equipment list prepared in basic design, considered ambient temperature shall be 55 degree centigrade. Therefore all mentioned 48 degrees in this document shall be modified to 55. also considered derating factor shall be related to 55 degree centigrade. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | محاسبات بر اساس آخرین لیست بار به روزرسانی گردیده است. |  |  | Noted and Closed.
8 | The calculated Load kVA during starting of biggest motor (on page 8, section 5.2) shall be calculated base on total apparent power. (219.8KVA is not total apparent power) |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | محاسبات بر اساس آخرین لیست بار به روزرسانی گردیده است. |  |  | Noted and Closed.
9 | The value of voltage dip base on appendix 3 shall be specified on page 9, section 5.3. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | محاسبات بر اساس آخرین لیست بار به روزرسانی گردیده است. |  |  | Noted and Closed.
10 | The used formula for calculating of apparent power for Motor Starting and Total sum of kVA delivered by generator to start shall be explained in detail on page 8, section 5.2. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | محاسبات بر اساس آخرین لیست بار به روزرسانی گردیده است. |  |  | Noted and Closed.
11 | Letter "Prime" shall be modified to "Continous" in following sentence on page 6: Diesel engine prime power shall be 445 kWm (net) / 455 kWm (gross) |  | BK-SUR-ENG-ELE-01-05638 | 2022-09-12 | اعمال گردید. |  |  | Noted and Closed.
12 | Page 7, section 4.2 conclusion: The conclusion for standby power shall be mentioned. Meanwhile the prime calculation is not needed and can be deleted. |  | BK-SUR-ENG-ELE-01-05638 | 2022-09-12 | اعمال گردید. |  |  | Noted and Closed.
13 | Page 7, section 4.3 conclusion: It shall be clarify Diesel engine standby power (490KW) has been mentioned base on which calculation? |  | BK-SUR-ENG-ELE-01-05638 | 2022-09-12 | اصلاح گردید. |  |  | Noted and Closed.
14 | If any changes in prerequsit documents such as load list this document shall be revised. |  | BK-SUR-ENG-ELE-01-05638 | 2022-09-12 | در صورت وجود تغییرات، این مدرک به روزرسانی خواهد شد. |  |  | Will be checked later.
15 | No Comment. Note: If any changes in rated power of equipment such as air compressor package, 110AC UPS, HVAC for control building, emergency lighting panel, etc, this document shall be rechecked and revised. |  | BK-SUR-ENG-ELE-02-07256 | 2023-03-25 | این مدرک بر اساس ترنسمیتال 2764 به روزرسانی و توان دیزل ژنراتور با توجه به تغییرات بار اضطراری محاسبه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: