## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: |  |  |  | MECHANICAL DATA SHEETS FOR SUMP PUMPS | [9 empty] | شماره صفحه: 1 از 5
053-073-9184 |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه
|  |  |  | BK | GCS | PEDCO | 120 | ME | DT |  | 0023 | D05
طرح نگهداشت و افزایش تولید 27 مخزن
MECHANICAL DATA SHEETS FOR SUMP PUMPS نگهداشت و افزایش تولید میدان نفتی بینک
D05 | SEP.2024 | IFA |  |  |  |  | V.Amjadi |  |  | M. Fakharian |  |  | M.Sadeghian
D04 | AUG.2024 | IFA |  |  |  |  | V.Amjadi |  |  | M. Fakharian |  |  | M.Sadeghian
D03 | OCT. 2023 | IFA |  |  |  |  | H.Ghadyani |  |  | M. Fakharian |  |  | S.Faramarzpour
D02 | DEC. 2022 | IFA |  |  |  |  | H. Adineh |  |  | M. Fakharian |  |  | M.Mehrshad
D01 | JAN. 2022 | IFA |  |  |  |  | H. Adineh |  |  | M. Fakharian |  |  | M.Mehrshad
D00 | DEC. 2021 | IFC |  |  |  |  | H. Adineh |  |  | M. Fakharian |  |  | M.Mehrshad
Rev. | Date | Purpose of Issue / Status |  |  |  |  | Prepared by: |  |  | Checked by: |  |  | Approved by: |  | CLIENT Approval
Class: 1 |  | CLIENT Doc. Number: F0Z-708854
status: |  |  | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## Record Sheet
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: |  |  |  |  | MECHANICAL DATA SHEETS FOR SUMP PUMPS | [10 empty] | شماره صفحه: 2 از 5
053-073-9184 |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک |  | سریال |  | نسخه
[5 empty] | BK | GCS | PEDCO | 120 | ME |  | DT |  | 0023 |  | D05
REVISION RECORD SHEET
|  | page | D00 | D01 | D02 | D03 | D04 | D05 |  | page |  | D00 |  | D01 | D02 | D03 | D04 | D05
|  | 1 | X | X | X | X | X | X |  | 65
|  | 2 | X | X | X | X | X | X |  | 66
|  | 3 | X | X | X | X |  |  |  | 67
|  | 4 | X |  | X | X | X |  |  | 68
|  | 5 | X |  | X | X | X | X |  | 69
|  | 6 | [7 empty] | 70
|  | 7 | [7 empty] | 71
|  | 8 | [7 empty] | 72
|  | 9 | [7 empty] | 73
|  | 10 | [7 empty] | 74
|  | 11 | [7 empty] | 75
|  | 12 | [7 empty] | 76
|  | 13 | [7 empty] | 77
|  | 14 | [7 empty] | 78
|  | 15 | [7 empty] | 79
|  | 16 | [7 empty] | 80
|  | 17 | [7 empty] | 81
|  | 18 | [7 empty] | 82
|  | 19 | [7 empty] | 83
|  | 20 | [7 empty] | 84
|  | 21 | [7 empty] | 85
|  | 22 | [7 empty] | 86
|  | 23 | [7 empty] | 87
|  | 24 | [7 empty] | 88
|  | 25 | [7 empty] | 89
|  | 26 | [7 empty] | 90
|  | 27 | [7 empty] | 91
|  | 28 | [7 empty] | 92
|  | 29 | [7 empty] | 93
|  | 30 | [7 empty] | 94
|  | 31 | [7 empty] | 95
|  | 32 | [7 empty] | 96
|  | 33 | [7 empty] | 97
|  | 34 | [7 empty] | 98
|  | 35 | [7 empty] | 99
|  | 36 | [7 empty] | 100
|  | 37 | [7 empty] | 101
|  | 38 | [7 empty] | 102
|  | 39 | [7 empty] | 103
|  | 40 | [7 empty] | 104
|  | 41 | [7 empty] | 105
|  | 42 | [7 empty] | 106
|  | 43 | [7 empty] | 107
|  | 44 | [7 empty] | 108
|  | 45 | [7 empty] | 109
|  | 46 | [7 empty] | 110
|  | 47 | [7 empty] | 111
|  | 48 | [7 empty] | 112
|  | 49 | [7 empty] | 113
|  | 50 | [7 empty] | 114
|  | 51 | [7 empty] | 115
|  | 52 | [7 empty] | 116
|  | 53 | [7 empty] | 117
|  | 54 | [7 empty] | 118
|  | 55 | [7 empty] | 119
|  | 56 | [7 empty] | 120
|  | 57 | [7 empty] | 121
|  | 60 | [7 empty] | 124
|  | 61 | [7 empty] | 125
|  | 62 | [7 empty] | 126
|  | 63 | [7 empty] | 127
|  | 64 | [7 empty] | 128

## Notes
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: |  |  | MECHANICAL DATA SHEETS FOR SUMP PUMPS | [8 empty] | شماره صفحه: 3 از 5
053-073-9184 |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | PEDCO | 120 | ME |  | DT | 0023 | D05
GENERAL NOTES
| 1 | Design Conditions: | Min./Max Design Temp.℃ |  |  |  |  | Max.Design Press.(barg)
|  |  |  | 5 / 85 |  |  |  |  | 2.5
| 2 | For electrical motor descriptions, refer to 'Specification For LV Electro Motors' Doc. No. BK-GNRAL-PEDCO-000-EL-SP-0010.
| 3 | For technical requirements of electrical LV motors refer to "Data sheets for LV induction motors" Doc.No; BK-GCS-PEDCO-120-EL-DT-0008"
Vendor shall fill in the blanks and return the completed data sheet along with his proposal.
| 4 | Vendor shall submit ITP (Inspection & Testing Plan) with his proposal.
| 5 | The motors,pump coupling and pump accessories shall be supplied from the project's approved vendor list (A.V.L.).
| 6 | Vendor is requested to confirm the material, or propose appropriate alternative.
| 7. | Mechanical seal data sheet shall fill in by vendor as per API 682. Pump Manufacturer shall supply all instrumentation for mechanical seals as per API 682 4th Edition and project requirements.
Also orifice with diameter 3mm to be considered by vendor for seal flushing.
| 8. | NPSH test shall be done & witnessed if the margin of NPSHr & NPSHa is less than 1.
| 9. | The Tie-in flanges shall conform to ASME B-16.5.
| 10. | Supplier to indicate which minimum flow pumps can achieve.
| 11. | Pumps shall be designed, fabricated, tested, and inspected in accordance with the requirements of ISO 5199 latest edition.
| 12. | Pump starts automatically with open delivery valve.
| 13. | Electrical motor shall be rated for the end of curve.
| 14. | The discharge line is 2".
| 15. | Material class of ‘I-1’, ‘I-2’,‘S-1’, ‘S-2’, ‘S-3’, ‘S-4’, ‘S-5’, ‘S-6’,'C-6' 'A-7' and 'A-8', which is defined in API 610 table H.1,
shall be provided with full chemical analysis and mechanical test certification to BS EN 10204:2004 "3.1".
Material class of ‘D-1’ and ‘D-2’, which is defined in API 610 table H.1 and also titanium materials shall be provided with
full chemical analysis and mechanical test certification to BS EN 10204:2004 "3.2".
| 16. | Based on project instrumentation specification, these equipments are classified as Type B (Connected to DCS/ESD):Centrifugal Pump Package
| 17. | Pump material shall be selected based on Annex H API 610 11th Edition. (vendor to confirm)
| 18 | Ultrasonic Test shall be performed for forged shaft.
| 19 | For pumps with vacuum suction pressure the minimum NPSH margin shall be 2 m. for other pumps the minimum NPSH margin shall be 1 m.
| 20 | Couplings shall be dry, flexible and spacer type.
| 21 | Bearing temperature shall be measured during mechanical run test.
| 22 | Max Allowable Pressure at Shut-Off is 2.5 barg.
| 23 | For site conditions refer to Process basis of design document; Doc.No: BK-GNRAL-PEDCO-000-PR-DB-0001.in data sheet.
| 25 | Minimum Design Metal Tem (MDMT) = 5℃.
| 26 | Vendor to provide the pump with mentioned flow rate or minimum available flow rate at market.
| 27 | Max. allow. Sound press. Level =85 dBA.
| 28 | Allowable external forces and moments on nozzle should be conformed to Spec. No.: BK-GCS-PEDCO-120-ME-SP-0004.
| 29 | All drain and vents (If any) to be manifolded, valved and routed to the skid edge.
| 30 | Range of ambient temperature: Min. ambient temperature: 5 °C , Max. ambient temperature: 50 °C
| 31 | Hydraulic power (Kw): 0.31
| 32 | For Instrumentation, Project specification 'Specification For Instrument and Control of package Unit System (PU)' Doc. No.BK-GNRAL-PEDCO-000-IN-SP-0004 and Specification
For Hazardous Area Classification; BK-GNRAL-PEDCO-000-SA-SP-0002 and other instrument specification which to be attached to MR shall be followed.
| 33 | The Sump pump is in pit. Sump dimentions have been considered in calculations of operating conditions. For further data refer to related P&ID;
BK-GCS-PEDCO-120-PR-PI-0017. and Calculation Note For Pumps; BK-GCS-PEDCO-120-PR-CN-0001.

## 1 (hidden)
Basic Design Study and FEED Package Preparation for Pazanan-2 Desalting Unit Refurbishment
Hirgan Energy Eng. Co. | [28 empty] | NISOC
Project No.: 53-51-91211 | [9 empty] | Document Title : Mechanical Data Sheet For Deaerated Water Pumps | [18 empty] | Contract No.: 53-73-1264
Consult. Proj. No.: 9104 | [9 empty] | Proj. |  |  |  | Loc. |  |  | Disc. |  |  | Type |  |  | Seq. |  |  | Rev. |  |  | Page No: 3 of 6
[10 empty] | 91211 |  |  |  | PZN |  |  | ME |  |  | DS |  |  | 421 |  |  | R00
CENTRIFUGAL PUMP FOR GENERAL SERVICE DATA SHEET (SI UNIT) P-702 A/B
APPLICABLE TO: | [7 empty] | l | PROPOSAL | [7 empty] | m | PURCHASE | [6 empty] | m | AS BUILT
FOR |  | NISOC | [10 empty] | UNIT | [11 empty] | Pazanan-2 Desalting
SITE | [12 empty] | NO. REQUIRED | [11 empty] | 2
SERVICE |  | Deaerated Water Pump | [10 empty] | PUMP SIZE, TYPE & NO. OF STAGES | [11 empty] | Centrifugal
VENDOR | [12 empty] | MODEL | [14 empty] | SERIAL NO.
Note: m Represents data to be completed by CONTRACTOR o by VENDOR [m] by VENDOR if not by CONTRACTOR
GENERAL
PUMPS TO OPERATE IN (PARALLEL) | [9 empty] | 1 |  |  | NO. MOTOR DRIVEN | [7 empty] | 2 |  |  |  | NO. DIESEL DRIVEN
(SERIES) WITH : | [12 empty] | PUMP ITEM NO. | [11 empty] | PUMP ITEM NO.
GEAR ITEM NO. | [12 empty] | MOTOR ITEM NO. | [11 empty] | DIESEL ITEM NO.
GEAR PROVIDED BY | [12 empty] | MOTOR PROVIDED BY | [7 empty] | Vendor |  |  |  | DIESEL PROVIDED BY
GEAR MOUNTED BY | [12 empty] | MOTOR MOUNTED BY | [7 empty] | Vendor |  |  |  | DIESEL MOUNTED BY
GEAR DATA SHEET NO'S | [12 empty] | MOTOR DATA SHEET NO'S | [11 empty] | DIESEL D.S. NO'S
APPLICABLE OVERLAY STANDARD | [9 empty] | ISO 5199
OPERATING CONDITIONS | [17 empty] | LIQUID
l | CAPACITY, NORMAL |  |  |  |  | 37 |  | m³/hr |  | RATED |  | 41 |  | m³/hr |  |  |  | l | TYPE OR NAME OF LIQUID | [8 empty] | Water
| OTHER | [16 empty] | LIQUIDS |  |  |  | m | TOXIC |  |  | m | FLAMMABLE |  |  |  |  | m | OTHER
l | SUCTION PRESSURE |  |  |  |  | (MAX/RATED) | [5 empty] | 4.5/-0.93 |  |  | Barg |  |  | l | PUMPING TEMPERATURE (PT) | [8 empty] | NORMAL |  |  | 51 |  |  | ˚C
l | DISCHARGE PRESSURE @ RATED FLOW | [10 empty] | 4.1 |  |  | Barg |  |  |  | MAXIMUM | [5 empty] | ˚C |  |  | MINIMUM | [5 empty] | ˚C
l | DIFFERENTIAL PRESSURE | [8 empty] | 5 |  |  | Bar |  |  |  |  | l | SPECIFIC GRAVITY | [7 empty] | 1 |  |  |  | @ | PT
l | DIFFERENTIAL HEAD | [7 empty] | 51 |  |  |  | m |  |  |  |  | m | MAXIMUM SPECIFIC GRAVITY | [11 empty] | @ |  |  | ˚C
l | NPSHA | [7 empty] | 2.54 |  |  |  | m |  |  |  |  | m | SPECIFIC HEAT | [10 empty] | CP (KJ/KG.˚C)
l | HYDRAULIC POWER | [7 empty] | 5.7 |  |  |  | KW |  |  |  |  | l | VAPOUR PRESSURE @ PUMPING TEMP | [10 empty] | 0.07 |  |  | Bara
SERVICE: |  | l | CONTINUOUS |  |  |  | m | INTERMITTENT | [9 empty] | l | VISCOSITY | [7 empty] | 1.5 |  |  |  |  | CP @PT
PROCESS VARIATION | [17 empty] | m | MAX VISCOSITY @ MIN TEMP | [10 empty] | cP @ COLD START
STARTING CONDITION | [17 empty] | m | CORROSIVE/EROSIVE AGENT
m | PARALLEL OPERATION CONDITION REQ'D | [16 empty] | m | CHLORIDE CONCENTRATION | [10 empty] | PPM
SITE AND UTILITY DATA | [17 empty] | m | H2S CONCENTRATION | [10 empty] | PPM
LOCATION | [17 empty] | CONVENTIONS
m | INDOOR |  | l | OUTDOOR |  |  | l | UNDER ROOF |  |  |  | m | PARTIAL SIDES |  |  |  |  | NPSH REFERENCE DATUM
l | UNHEATED |  |  | m | HEATED |  |  | m | GRADE |  |  | m | MEZZANINE |  |  |  |  | l | PUMP CENTRELINE | [6 empty] | m | UNDERSIDE OF BASEPLATE
m | ELECTRICAL AREA CLASSIFICATION | [16 empty] | m | SUCTION NOZZLE CENTRELINE | [8 empty] | m | OTHER
TEMP CLASS | [5 empty] | GAS GROUP |  |  |  | ZONE |  | SAFE | [10 empty] | l | ESTIMATED POWER
m | WINTERISATION REQ'D | [7 empty] | l | TROPICALISATION REQ'D | [7 empty] | ESTIMATED PUMP EFFICIENCY
SITE DATA: | [17 empty] | ESTIMATED RATED PUMP ABSORBED POWER | [15 empty] | KW
m | ELEVATION |  |  |  | 298 |  | m |  | m | BAROMETER, Bara | [5 empty] | 759.8 |  | ESTIMATED PUMP ABSORBED POWER AT MAX. SG | [15 empty] | KW
m | RANGE OF AMBIENT TEMPS: MIN/MAX | [9 empty] | -2.8/50.6 |  |  | ˚C |  |  |  | DRIVER RATING FACTOR
m | RELATIVE HUMIDITY: MAX/MIN | [7 empty] | 93/10 |  |  |  | % |  |  |  |  | ESTIMATED DRIVER RATING | [15 empty] | KW
UNUSUAL CONDITIONS | [17 empty] | RATED PERFORMANCE
l | DUST |  | m | FUMES |  |  |  | m | OTHER | [8 empty] | o | rpm
UTILITIES | [17 empty] | o | PROPOSAL CURVE NO
STEAM: | [17 empty] | o | IMPELLER Dia mm: | [8 empty] | RATED
ELECTRICITY | [21 empty] | MAX. | [5 empty] | MIN.
|  |  | DRIVERS |  |  |  | HEATING |  |  | CONTROL |  |  |  | SHUTDOWN |  |  |  | o | RATED POWER |  |  |  |  | KW |  |  |  | EFFICIENCY |  |  |  | %
|  | MAIN | [15 empty] | o | MINIMUM CONTINUOUS FLOW
VOLTAGE |  | 400 | [16 empty] | THERMAL | [6 empty] | m³/H |  | STABLE | [5 empty] | m³/H
HERTZ |  | 50 | [15 empty] | o | MAX HEAD RATED IMPELLER | [14 empty] | m
PHASE |  | 3 | [15 empty] | o | MAX POWER RATED IMPELLER | [14 empty] | KW
COOLING WATER | [5 empty] | (NOT AVAILABLE) | [11 empty] | o | NPSH REQUIRED AT RATED CAPACITY | [14 empty] | m
TEMP INLET | [5 empty] | ˚C |  |  | MAX RETURN | [6 empty] | ˚C |  | o | SUCTION SPECIFIC SPEED | [14 empty] | (rpm,m³/H,m)
PRESS NORMAL | [5 empty] | Barg |  |  | DESIGN | [6 empty] | Barg |  | o | MAX SOUND PRESSURE LEVEL | [14 empty] | dB(A)
MIN RETURN | [5 empty] | Barg |  |  | MAX ALLOW DP | [6 empty] | Bar
WATER SOURCE
INSTRUMENT AIR PRESSURE (Barg)
MAX. |  |  |  |  | NORMAL | [5 empty] | MIN.

## 2 (hidden)
Basic Design Study and FEED Package Preparation for Pazanan-2 Desalting Unit Refurbishment
Hirgan Energy Eng. Co. | [24 empty] | NISOC
Project No.: 53-51-91211 | [9 empty] | Document Title : Mechanical Data Sheet For Deaerated Water Pumps | [14 empty] | Contract No.: 53-73-1264
Consult. Proj. No.: 9104 | [9 empty] | Proj. |  |  |  | Loc. |  | Disc. | Type |  |  | Seq. |  | Rev. |  |  | Page No: 4 of 6
[10 empty] | 91211 |  |  |  | PZN |  | ME | DS |  |  | 421 |  | R00
CENTRIFUGAL PUMP FOR GENERAL SERVICE DATA SHEET (SI UNIT) P-702 A/B
CONSTRUCTION | [16 empty] | MATERIALS
[m] |  | MAIN CONNECTIONS
| SERVICE |  |  | SIZE |  | ANSI RATING |  |  |  | FACING |  |  | POSITION |  |  |  | [l] |  | BARREL / CASE | [7 empty] | A 278 Class 30
SUCTION |  |  |  |  | 6" | 150 # | [10 empty] | [l] |  | INNER CASE | [7 empty] | A 278 Class 30
DISCHARGE |  |  |  |  | 4" | 150 # | [10 empty] | [l] |  | IMPELLER | [7 empty] | A 278 Class 30
BAL. DRUM | [16 empty] | [l] |  | WEAR RINGS |  |  |  | CASE |  |  |  | A 278 Class 30
[23 empty] | IMPELLER |  |  |  | A 278 Class 30
[17 empty] | [l] |  | SHAFT | [6 empty] | A 696 GrB40
[m] |  | OTHER CONNECTIONS | [14 empty] | [l] |  | SLEEVE | [7 empty] | A 278 Class 30
| SERVICE |  |  |  |  | NO |  |  | SIZE |  |  |  |  | TYPE |  |  | [m] |  | DIFFUSERS
DRAIN | [16 empty] | [m] |  | COUPLING HUBS
VENT | [16 empty] | [m] |  | COUPLING SPACER
PURGE | [16 empty] | [m] |  | COUPLING DIAPHRAGMS
SEAL VENT | [16 empty] | o |  | API BASEPLATE NO / MATERIAL
[17 empty] | l |  | VERTICAL LEVELLING SCREWS
CASING | [16 empty] | l |  | HORIZONTAL POSITIONING SCREWS
MOUNTING
[l] |  | CENTRELINE | [5 empty] | [m] |  | NEAR CENTRELINE
[m] |  | FOOT | [5 empty] | [m] |  | SEPARATE MOUNTING PLATE
[m] |  | VERTICAL | [5 empty] | [m] |  | SUMP
[m] |  | IN-LINE
SPLIT | [16 empty] | BEARINGS AND LUBRICATION
[m] |  | AXIAL | [5 empty] | [l] |  | RADIAL | [6 empty] | BEARING (TYPE / ISO NUMBER)
TYPE | [16 empty] | [m] |  | RADIAL
[l] |  | SINGLE VOLUTE | [5 empty] | [m] |  | DOUBLE VOLUTE | [6 empty] | [m] |  | THRUST
[m] |  | BARREL | [7 empty] | DIFFUSER | [6 empty] | m |  | REVIEW AND APPROVE THRUST BEARING SIZE
[m] |  | STAGGERED VOLUTES | [5 empty] | [m] |  | VERTICAL DOUBLE CASING | [6 empty] | LUBRICATION
IMPELLER MOUNTING | [16 empty] | [m] |  | GREASE |  | [m] |  | FLOOD |  |  | [m] |  | PURGE OIL MIST
| [m] |  | BETWEEN BEARINGS | [7 empty] | [l] |  | OVERHUNG |  |  |  | [m] |  | FLINGER |  | [l] |  | RING OIL |  |  | [m] |  | PURE OIL MIST
| [m] |  | IMPELLERS INDIVIDUALLY SECURED | [13 empty] | [m] |  | CONSTANT LEVEL OILER
CASE PRESSURE RATING | [16 empty] | [m] |  | PRESSURE |  |  |  |  | m | API 614
MAXIMUM ALLOWABLE WORKING PRESS | [16 empty] | [m] |  | OIL VISCOSITY ISO GRADE
o | MAOP | [5 empty] | Barg |  |  |  |  | @ |  |  | ˚C |  | [m] |  | OIL HEATER REQ'D |  |  |  |  | m | STEAM |  |  | m | ELECTRIC
m | SUCTION PRESSURE REGIONS OF MULTISTAGE OR DOUBLE CASING PUMPS | [15 empty] | m | OIL PRESS. TO BE GREATER THAN COOLANT PRESSURE
TO BE DESIGNED FOR MAXIMUM ALLOWABLE WORKING PRESS.
o | HYDROTEST PRESSURE | [8 empty] | Barg
ROTATION (VIEWED FROM COUPLING END)
| o | CW (CLOCKWISE) |  |  |  |  | o | CCW (COUNTER-CLOCKWISE) | [8 empty] | COUPLINGS
SHAFT | [16 empty] | [m] |  | MAKE
ALL PUMPS | [16 empty] | [m] |  | MODEL
o | SHAFT DIAMETER AT SEAL SLEEVE | [14 empty] | mm | [m] |  | LUBRICATION
o | SHAFT DIAMETER AT COUPLING | [14 empty] | mm | [m] |  | SERVICE FACTOR
o | SHAFT DIAMETER AT RADIAL BEARING(S) | [14 empty] | mm | [m] |  | SPACER LENGTH | [9 empty] | mm
o | SHAFT DIAMETER AT IMPELLER | [14 empty] | mm | o |  | CPLG RATING (KW / 100 rpm)
OVERHUNG PUMPS | [16 empty] | m |  | COUPLING PER API 671
o | SPAN BETWEEN BEARING CENTRELINE & IMPELLER | [14 empty] | mm | [l] |  | DYNAMIC BALANCING | [5 empty] | o | BALANCE CLASS
o | SHAFT DIAMETER BETWEEN BEARINGS | [14 empty] | mm | DRIVER HALF COUPLING MOUNTED BY:
o | SPAN BETWEEN BEARING CENTRELINES | [14 empty] | mm | l | PUMP MANUFACTURER | [5 empty] | m | DRIVER MANUFACTURER
BETWEEN BEARING PUMPS | [16 empty] | m | CONTRACTOR
o | SPAN BETWEEN BEARING CENTRELINES | [14 empty] | mm | NOISE
o | SPAN BETWEEN BEARING CENTRELINES | [14 empty] | mm | l | MAXIMUM SOUND PRESSURE LEVEL | [9 empty] | 85 | @ | 1m
[17 empty] | m | SEE SEPARATE DATA SHEET

## 3 (hidden)
Basic Design Study and FEED Package Preparation for Pazanan-2 Desalting Unit Refurbishment
Hirgan Energy Eng. Co. | [24 empty] | NISOC
Project No.: 53-51-91211 | [6 empty] | Document Title : Mechanical Data Sheet For Deaerated Water Pumps | [17 empty] | Contract No.: 53-73-1264
Consult. Proj. No.: 9104 | [6 empty] | Proj. |  |  |  | Loc. |  |  | Disc. |  | Type |  |  | Seq. |  |  | Rev. |  |  | Page No: 5 of 6
[7 empty] | 91211 |  |  |  | PZN |  |  | ME |  | DS |  |  | 421 |  |  | R00
CENTRIFUGAL PUMP FOR GENERAL SERVICE DATA SHEET (SI UNIT) P-702 A/B
MOTOR DRIVE | [14 empty] | SURFACE PREPARATION & PAINTING
[m] |  | VENDOR | [12 empty] | [l] |  | VENDOR'S STANDARD
o |  | RATING |  |  |  | KW |  |  | [m] |  | rpm |  |  |  | [m] |  | OTHER
[l] |  | HORIZONTAL |  |  |  | [m] |  | VERTICAL | [6 empty] | l | PAINTING SHALL BESUITABLE FOR HOT AND HUMID CONDITIONS
o |  | FRAME SIZE | [12 empty] | PUMP
[m] |  | SERVICE FACTOR |  | 1.25 | [10 empty] | [l] |  | PUMP SURFACE PREPARATION TO
[l] |  | VOLTS | 400 | l |  |  | PHASE 3 |  |  |  | l | 50 HERTZ |  |  | [l] |  | PRIMER
[m] |  | TYPE | [12 empty] | [l] |  | FINISH COAT
[m] |  | ENCLOSURE | [12 empty] | BASEPLATE
[m] |  | TYPE OF PROTECTION |  |  |  | IP 55 | [8 empty] | [l] |  | BASEPLATE SURFACE PREPARATION TO
[m] |  | MINIMUM STARTING VOLTAGE | [6 empty] | 80 |  |  | % |  |  | [l] |  | PRIMER
[m] |  | TEMPERATURE RISE |  | -5 | ˚C |  |  |  | OVER |  | 55 |  | ˚C |  | [l] |  | FINISH COAT
[m] |  | FULL LOAD AMPS | [12 empty] | GROUTING |  |  |  |  | m | YES |  | l | NO
[m] |  | LOCKED ROTOR AMPS | [10 empty] | % FLC |  | REQUIRED
[m] |  | INSULATION CLASS | [12 empty] | [m] |  |  | GROUT SURFACE PREPARATION TO
[m] |  | STARTING METHOD | [12 empty] | [m] |  |  | EPOXY PRIMER
[m] |  | BEARINGS | [12 empty] | [m] |  |  | REMARKS
[m] |  | LUBRICATION
[m] |  | 2X THRUST RATING | [12 empty] | SHIPMENT
VERTICAL SHAFT |  |  |  |  | [m] |  | SOLID |  |  | [m] |  | HOLLOW |  |  | l | DOMESTIC |  |  | m | EXPORT |  |  | l | EXPORT BOXING REQUIRED
o | VERTICAL THRUST CAPACITY | [13 empty] | l | OUTDOOR STORAGE FOR MORE THAN MONTHS
| UP |  | KN |  |  |  | DOWN |  |  |  |  | KN |  |  | SPARE ROTOR ASSEMBLY PACKAGED FOR
m | SEE SEPARATE DATA SHEET NO | [13 empty] | [m] |  | HORIZONTAL STORAGE | [6 empty] | [m] |  | VERTICAL STORAGE
[15 empty] | [l] |  | TYPE OF SHIPPING PREPARATION | [9 empty] | AS MAIN EQUIPMENT
SPARE PARTS | [14 empty] | WEIGHTS
l | START-UP | [13 empty] | MOTOR DRIVEN
l | OPERATIONAL (RECONDITIONING) | [5 empty] | 3 YEARS | [9 empty] | WEIGHT OF PUMP | [10 empty] | Kg
m | INSURANCE (CRITICAL SERVICE) | [15 empty] | WEIGHT OF BASEPLATE | [10 empty] | Kg
l | SPECIFY PER SPEC. | [15 empty] | WEIGHT OF MOTOR | [10 empty] | Kg
[17 empty] | WEIGHT OF GEARBOX | [10 empty] | Kg
[17 empty] | TOTAL WEIGHT | [10 empty] | Kg
TURBINE DRIVEN
[17 empty] | WEIGHT OF BASEPLATE | [10 empty] | Kg
[17 empty] | WEIGHT OF TURBINE | [10 empty] | Kg
[17 empty] | WEIGHT OF GEARBOX | [10 empty] | Kg
[17 empty] | TOTAL WEIGHT | [10 empty] | Kg
REMARKS
OTHER CONTRACTOR REQUIREMENTS
[15 empty] | l | CO-ORDINATION MEETING REQUIRED
[15 empty] | m | VENDOR TO REVIEW FOUNDATION DRAWING
[15 empty] | m | VENDOR TO REVIEW PIPING DRAWINGS
[15 empty] | m | VENDOR TO OBSERVE PIPING CHECKS
[15 empty] | m | VENDOR TO OBSERVE INITIAL ALIGNMENT CHECK
[15 empty] | m | VENDOR TO CHECK ALIGNMENT AT OPERATING TEMP.
[15 empty] | [m] |  | ROTOR TO BE BALANCED DURING
ASSEMBLY OF EACH ELEMENT
[15 empty] | m | VENDOR TO DEMONSTRATE
VIBRATION AT MINIMUM FLOWRATE
[15 empty] | [m] |  | LATERAL RESPONSE ANALYSIS REQUIRED
[17 empty] | m | PUMP ONLY | [5 empty] | m | ALL EQUIPMENT
[15 empty] | [m] |  | CRITICAL SPEED ANALYSIS
[15 empty] | [m] |  | STIFFNESS MAP OF UNDAMPED ROTOR
[15 empty] | [m] |  | TORSIONAL ANALYSIS
[15 empty] | l | PROGRESS REPORTS REQUIRED

## 4 (hidden)
Basic Design Study and FEED Package Preparation for Pazanan-2 Desalting Unit Refurbishment
Hirgan Energy Eng. Co. | [17 empty] | NISOC
Project No.: 53-51-91211 | [6 empty] | Document Title : Mechanical Data Sheet For Deaerated Water Pumps | [10 empty] | Contract No.: 53-73-1264
Consult. Proj. No.: 9104 | [6 empty] | Proj. |  |  |  | Loc. |  |  | Disc. | Type | Seq. | Rev. | Page No: 6 of 6
[7 empty] | 91211 |  |  |  | PZN |  |  | ME | DS | 421 | R00
CENTRIFUGAL PUMP FOR GENERAL SERVICE DATA SHEET (SI UNIT) P-702 A/B
QA INSPECTION & TEST
l | CONTRACTOR REVIEW OF VENDOR'S QA PROGRAMME
l | PERFORMANCE CURVE APPROVAL
l | SHOP INSPECTION
TEST | [7 empty] | REQ'D |  |  | WITN'D |  |  | OBS'D
l | HYDROSTATIC | [6 empty] | l |  | m |  |  | m
l | PERFORMANCE | [6 empty] | l |  | l |  |  | m
m | NPSH |  | # |  |  |  |  | m |  | m |  |  | m
l | COMPLETE UNIT | [6 empty] | l |  | l |  |  | m
m | DISMANTLE & INSPECT AFTER TEST | [6 empty] | m |  | m |  |  | m
m | CLEANLINESS PRIOR TO FINAL ASS'Y | [6 empty] | m |  | m |  |  | m
m | PIPE LOAD TEST | [6 empty] | m |  | m |  |  | m
l | MECHANICAL RUN TEST | [6 empty] | l |  | l |  |  | m
l | SOUND LEVEL TEST | [6 empty] | l |  | m |  |  | m
l | MATERIAL CERTIFICATION REQUIRED
| l | CASING |  | l |  | IMPELLER |  |  |  |  | l | SHAFT
| m | OTHER
l | CASTING REPAIR PROCEDURE APPROVAL REQUIRED
[l] |  | INSPECTION REQUIRED FOR NOZZLE WELDS
| [l] |  | MAGNETIC PARTICLE |  |  |  |  | [m] |  | LIQUID PENETRANT
| [l] |  | RADIOGRAPHIC |  |  |  |  | [m] |  | ULTRASONIC
[l] |  | INSPECTION REQUIRED FOR CASTINGS
| [l] |  | MAGNETIC PARTICLE |  |  |  |  | [l] |  | LIQUID PENETRANT
| [m] |  | RADIOGRAPHIC |  |  |  |  | [l] |  | ULTRASONIC
m | CHARPY IMPACT TEST REQUIRED
m | INSPECTION REQUIRED FOR SEAL PIPING
| m | MAGNETIC PARTICLE | [5 empty] | l | LIQUID PENETRANT
| m | RADIOGRAPHIC | [5 empty] | m | ULTRASONIC
m | HARDNESS TEST REQUIRED FOR
m | SURFACTANT HYDROTEST
l | VENDOR TO SUBMIT TEST PROCEDURES FOR REVIEW.
l | RECORD FINAL ASSEMBLY RUNNING CLEARANCES
l | VENDOR TO MAINTAIN RECORDS FOR
| m | 5 YEARS |  | l | 10 YEARS
REMARKS

## P 2203 A,B-ISO (1)
NISOC | [10 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: | [10 empty] | MECHANICAL DATA SHEETS FOR SUMP PUMPS | [15 empty] | شماره صفحه: 4 از 5
053-073-9184 | [10 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات | رشته |  | نوع مدرک |  | سریال |  |  | نسخه
[11 empty] | BK |  | GCS |  | PEDCO |  | 120 | ME |  | DT |  | 0023 |  |  | D05
ISO Std. 5199 CENTRIFUGAL PUMP DATA SHEET (SI UNIT)
Corporate name | [5 empty] | Centrifugal pump Data sheet | [26 empty] | Rev.:
NISOC | [32 empty] | Data:
Name:
Plant: |  | BINAK GCS | [16 empty] | Service: | [5 empty] | Drain Water Pump
[19 empty] | Ref. Standards: | [5 empty] | ISO 5199, IPS-M-PM-115
[19 empty] | Ref. Spec. No. : | [5 empty] | BK-GCS-PEDCO-120-ME-SP-0004
|  |  | No. req. |  |  | Pump type |  |  |  | Eq. API-610 Type | [5 empty] | Mfr. serial No. |  |  | Kind of driver |  |  |  |  | Drive, type, size | [8 empty] | Item No.
Operation |  |  | 1 |  |  | Vertical |  |  |  | VS4(VTC) | [8 empty] | Motor |  |  |  |  | LV Induction Electric Motor | [8 empty] | P-2203 A/B
Standby |  |  | 1
Drawings |  |  | Installation dimension | [15 empty] | Pump weight | [9 empty] | Pump Content
|  |  | Assembly pump | [15 empty] | Customer |  |  |  | Enquiry No. | [9 empty] | Date
|  |  | Assembly shaft seal | [19 empty] | Order No. | [9 empty] | Date
|  |  | Piping |  | Auxiliary system | [13 empty] | Supplier |  |  |  | Proposal No. | [9 empty] | Date
[5 empty] | Shaft seal | [17 empty] | Contract No. | [9 empty] | Date
Test (4) |  |  | Material (17) |  |  |  | Hydrostatic |  |  |  |  | Inspection |  |  |  |  | Perform. |  | NPSH (8) |  |  |  | Sound Level |  |  |  | Final inspection |  |  |  |  | Approved documents
Refer. |  |  | ISO 5199 |  |  |  | ISO 5199 |  |  |  |  | ISO 5199 |  |  |  |  | ISO 5199 |  | ISO 5199 | [7 empty] | ISO 5199 |  |  |  |  | ISO 5199
Witn. by |  |  | Certified |  |  |  | Witnessed |  |  |  |  | Witnessed |  |  |  |  | Witnessed |  | Witnessed |  |  |  | NOTE 27 |  |  |  | Certified |  |  |  |  | Certified
Operating Condition (NOTE 12)
Liquid | [5 empty] | Drain Water | [5 empty] | Flow |  |  |  |  | rated |  | 5.5 |  | m³/h |  | NPSH at rated flow | [5 empty] | Plant- NPSHA |  |  |  | 9.4 | m
Solids |  |  | Type | [13 empty] | normal |  | 5 |  | m³/h | [7 empty] | Pump- NPSH3 |  |  |  |  | m
|  |  | %of mass | [13 empty] | min. |  |  |  | m³/h |  | Pump speed rated | [10 empty] | rpm
Corrosion by | [11 empty] | Minimum flow required | [8 empty] | m³/h |  | Pump efficiency rated | [10 empty] | %
Op. Temp. (Min. / Max.) | [5 empty] | 5 / 50 |  |  |  | °C |  | Inlet gauge pressure |  |  |  |  | min. |  | 0.01 |  | barg |  | Pump power input rated (NOTE 2) | [10 empty] | kW
pH-value at Top | [16 empty] | max. |  | 0.1 |  | barg |  | Pump power input | [5 empty] | rated impeller dia. |  |  |  |  | kW
Density at Top | [5 empty] | 1024 |  |  |  | kg/m³ |  | Outlet gage pressure rated | [6 empty] | 2 |  | barg | [7 empty] | max. impeller dia. |  |  |  |  | kW
Vapour press. at Max. T | [5 empty] | 0.1 |  |  |  | bara |  | Differential pressure rated | [6 empty] | 2 |  | bar |  | Electric. Driver power output rated | [10 empty] | kW
Kinematic vis. at Top | [5 empty] | 0.5 |  |  |  | cP |  | Total head rated | [6 empty] | 19.9 |  | m |  | Steam turbine power output rated | [10 empty] | kW
Specific heat at Top | [9 empty] | J/Kg.K |  | Shut-off head | [8 empty] | m |  | Performance curve No.
Construction Features
Design | [9 empty] | barg |  | Max. allowable work press | [8 empty] | barg |  | Cooling water condition | [5 empty] | N.A.
Number of Stages | [11 empty] | Test pressure | [6 empty] | 1.5 x MAWP |  | barg |  | Cooling (C) Series (s) | [5 empty] | N.A.
Self priming | [11 empty] | Inlet Flange |  |  | Size/Position | [7 empty] | Heating (H), Parallel (p) | [5 empty] | C | H | S | P | Quantity
Impeller diameter |  |  | max | [6 empty] | mm |  |  |  |  | Rating/facing | [7 empty] | Bearing
|  |  | rated | [6 empty] | mm |  | Outlet Flange |  |  | Size/Position |  |  |  | 2" / Up |  |  |  | Seal Chamber
|  |  | min | [6 empty] | mm |  |  |  |  | Rating/facing (14) |  |  |  | 150# / RF |  |  |  | Cooler for seal flush
Pump length vertical pumps | [9 empty] | mm |  | Vent connection | [10 empty] | Oil cooler
Barrel dia. vertical pumps | [9 empty] | mm |  | Drain connection | [10 empty] | Flush | [5 empty] | Liquid |  |  |  | Quantity
Casing split | [11 empty] | Shaft seal manufacture | [10 empty] | Lantern ring
Casing seal type | [11 empty] | Type, size (NOTE 7) | [6 empty] | Mech. Seal |  |  |  | Mechanical ring
Impeller type | [11 empty] | Flush plan (VTC) | [6 empty] | 11+61 |  |  |  | Gland/Seal plate | [5 empty] | N/A
Casing support | [11 empty] | Material code | [10 empty] | Coupling (NOTE 20) |  |  | Manufacture
Rotation(looking from driver) | [11 empty] | Soft packing ring dimension | [13 empty] | Type, Size
Axial thrust reduction by | [11 empty] | Rad. Bearing |  |  |  |  | Type | [8 empty] | Diameter max | [7 empty] | mm
Total clearance |  |  | Impeller | [6 empty] | mm |  | Axial. Bearing |  |  |  |  | Size | [8 empty] | Spacer length | [7 empty] | mm
|  |  | Bal. Drum | [6 empty] | mm |  | Line shaft bearing | [10 empty] | Baseplate
|  |  | Shaft bushes | [6 empty] | mm |  | Bearing bracket No. | [10 empty] | Anchor bolts supplied by | [5 empty] | Vendor
|  |  | Wear plate | [6 empty] | mm |  | Lubrication | [10 empty] | Driver |  | Supplied by |  |  |  | Vendor
Wall thickness rot sheath / stat. cas | [11 empty] | Lubrication device | [12 empty] | Mounted by |  |  |  | Vendor
Site and Utility Data (NOTES 23,24)
Location |  |  |  | m | Partial sides |  |  |  | l | Outdoor |  |  | l | Unheated |  |  |  | Site data: |  |  |  | Elevation | [5 empty] | m | Barometer |  |  |  |  | mbar
m | Winterization REQ'D | [7 empty] | m | Tropicalization REQ'D | [7 empty] | Range of ambient temps: MIN/MAX | [10 empty] | 5/50 |  |  |  |  | ˚C
Unusual condition | [6 empty] | m | Dust |  | m | Fumes |  |  | m | Others |  |  | Relative humidity: MIN/MAX | [10 empty] | 0/100 |  |  |  |  | %
Driver |  | Volt. |  | 400 |  |  | Hertz |  |  | 50 |  |  |  | Phase |  | 3 |  | Max Voltage Variation (NOTE 24) | [10 empty] | ± 10%
Type of protection | [17 empty] | Max Frequency Variation (NOTE 24) | [10 empty] | ± 5%
Temperature rise class / Insulation class | [13 empty] | Zone 1 , IIB , T3 |  |  |  | Max Volt. and Frequency Variation together | [10 empty] | ± 10%

## P 2203 A,B-ISO (2)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: |  |  |  |  | MECHANICAL DATA SHEETS FOR SUMP PUMPS | [13 empty] | شماره صفحه: 5 از 5
053-073-9184 |  |  |  |  | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک | سریال |  | نسخه
[5 empty] | BK |  | GCS |  | PEDCO | 120 |  | ME |  | DT | 0023 |  | D05
ISO Std. 5199 CENTRIFUGAL PUMP DATA SHEET (SI UNIT)
Material (VTC)
API class |  |  | S-6 | (According to API-610) |  | (NOTES 6,15,17)
Casing | [5 empty] | Bearing bush | [9 empty] | Mecan. Seal |  | Gland plate & gasket
Discharge casing | [5 empty] | Balance disc-drum | [11 empty] | Rotor ring |  | Inner/outer
Suction casing | [5 empty] | Bal. counter disc-drum bus. | [11 empty] | Static ring |  | Inner/outer
Stage casing | [5 empty] | Contrain.shell / Stat.casing | [11 empty] | Spring or bellow
Suction impeller | [5 empty] | Rotor sheath / can | [11 empty] | Seal metal parts
Impeller | [5 empty] | Magnet material | [11 empty] | Rotary & Static ring seats
Diffuser | [5 empty] | Barrel | [9 empty] | Stuffing box |  | Gland Plate
Wear ring casing | [5 empty] | Column pipe | [11 empty] | Soft packing ring
Wear ring impeller | [5 empty] | Bearing bracket | [11 empty] | Lantern ring
Wear plate / lining | [5 empty] | Motor stool | [9 empty] | Shaft sleeve
Case bush | [5 empty] | Coupling | [9 empty] | Throat bush
Casing gaskets | [5 empty] | Coupling guard | [9 empty] | Paint | According to "Specification for Painting"; Doc. No. BK-GNRAL-PEDCO-000-PI-SP-0006
Shaft | [5 empty] | Base plate
Sump Arrangement (Note 33)
Sump Dimensions:
|  | Grade Elevation | [5 empty] | 1 |  |  | m
|  | Low Liquid Level | [5 empty] | 2 | 0.1 |  | m
|  | C.L. Of Discharge | [5 empty] | 3 |  |  | m
|  | Sump Depth | [5 empty] | l1 | 0.65 |  | m
|  | Pump Length | [5 empty] | l2 |  |  | m
|  | Grade to Disch. | [5 empty] | l3 |  |  | m
|  | Grade to Low Liquid Level | [5 empty] | l4 |  |  | m
|  | Grade to 1st Stg Impl'r. | [5 empty] | l5 | 0.5 (VTC) |  | m
|  | Submergence Req'd | [5 empty] | l6 |  |  | m
|  | Sump Diameter | [5 empty] | Fd |  |  | m
Fd
Remarks
For Pump schematic and P&ID refer to BK-GCS-PEDCO-120-PR-PI-0017. and calculation note for pumps; BK-GCS-PEDCO-120-PR-CN-0001.
| Customer | [11 empty] | Supplier
| Prepared (Data / Dep/ Signature) |  |  |  | Checked (Data / Dep/ Sign. | [7 empty] | Prepared (Data / Dep/ Signature) | [5 empty] | Checked (Data / Dep/ Sign.)
D05