## Reply Sheet
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0023 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2755 |  |  | Transmital Date: 8/18/2024
Document Title: Mechanical Data Sheets For Sump Pumps |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-ME-TR-2755 |  |  | Transmital Date: 8/18/2024
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-ME-DT-0023_D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
| همانگونه که در نامه پیشین ( 02/2294/333186 مورخ 1402/08/20) بیان گردید،با توجه به آلوده بودن آبهای سطحی، انتخاب کلاس I-2 مطابق با Annex G استاندارد API 610 صحیح نیست. |  | 1403-2294-244885 | 1403/06/28 | نقطه نظر کارفرمای محترم مد نظر قرار گرفت و کلاس مدرک به S-6 تغییر یافته است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: