## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-HV-PY-0014 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2526 |  |  | Transmital Date: 1/1/2024
Document Title: HVAC System Layout & For Extension of Existing Control Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-HV-TR-2526 |  |  | Transmital Date: 1/1/2024
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-HV-PY-0014_D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
HVAC comments :
1 | Find the attached file . |  | BK-SUR-ENG-HVC-02-08942 | 2024-01-13 | HVAC System Layout For Extension of Existing Control Building Totally Revised.
Electrical comments :
1 | ورودي و خروجي هوا به اتاق باطري مطابق توصيه IPS-E-EL-100 بخش 7.6.7.3 بايستي در دوسمت مخالف اتاق قرار داده شود. ورودي در پايين ديوار و خروجي در بالاي ديوار مقابل تا تعويض هوا بخوبي انجام شود. در طراحي انجام شده خروجي هوا در سقف قرار داده شده كه عملا تعويض هواي نيمي از اتاق انجام نخواهد شد. |  | BK-SUR-ENG-HVC-02-08942 | 2024-01-13 | Noted.
| ارتفاع محل قرارگيري دريچه ها در نقشه ها مشخص نيست. |  | BK-SUR-ENG-HVC-02-08942 | 2024-01-13 | Noted.
Arch. Comments
1 | Find the attached file . |  | BK-SUR-ENG-HVC-02-08942 | 2024-01-13 | HVAC System Layout For Extension of Existing Control Building Totally Revised.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: