## Sheet1
General | [9 empty] | Valve | [20 empty] | Actuator (Safety factor 25%) | [5 empty] | Airset |  |  | Positioner | Solenoid | [8 empty] | Limit Switch | [7 empty] | Other Accessories | [9 empty] | options
Item No. | Tag Number | Line Size Inlet size and schedule | Line Size Outlet size and schedule | Corrosion Allowance (mm) | Design Pressure (Barg) | Design Temperature (°C) | Inlet Pressure (Barg) | Inlet Temperature (°C) | Qty | Valve Type | Bore type | Mounting type | Valve Size | Inlet Connection | Outlet Connection | Body Material | Bonnet Material | Bolt and Nut | NACE | Ball Material | Seat Type | Seat Material | Shaft Type | Shaft Material | Packing | Gasket | Entry | Bonnet Type | Leakage | Lifting Lug | Actuator Type | Function | Air Supply pressure | Fail Action | Stroke time | Handwheel | Connection | Filter | Gauge | Positioner | Type | Body mat. | IP | Explosion protection | Elec. connection | Manual reset | Power supply | SIL3 REQUIREMENTS | Pneu. Connection | Type | Qty | Contact / Rating | Position | Enclosure material | IP | Explosion protection | Elec. Connection | Pilot Valve | Booster | Lock valve | fusible leakage | block relay | quick exhust | filter regulator | volume tank | mechanical position indicator | manual pneumatic bypass valve for solenoid valve | ANSI/FCI LEAKAGE CLASS | HYDRO PRESSURE | FUNCTIONAL TEST | PASSIVE FIRE PROTECTION | API 6FA REQUIREMENTS | SIL3 REQUIREMENTS | PARTIAL STROKING VALVE TEST | Control box | Limit stop
Table 1 | ESDV-2101 | 6" , SCH: 80 | 6" , SCH: 80 | 6 | - | 175 | 7.5 | 26.67~46.11 | 1 | Ball valve | Full bore | Trunnion Mounted | 6" | 6" /300# | 6" /300# | ASTM A105 | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 6 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-64 | EEx "d" ,IIB T3 | ISO M20 x 1.4 | Yes | 23 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes (Key operated) | Yes (junction box Eexd is included) | Yes
Table 2 | ESDV-2102 | 8" , SCH: 100 | 8" , SCH: 100 | 6 | - | 175 | 7.5 | 15.5 ~ 32 | 1 | Ball valve | Full bore | Trunnion Mounted | 8" | 8" /600# | 8" /600# | ASTM A105 | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 9 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes (Key operated) | Yes (junction box Eexd is included) | Yes
Table 3 | ESDV-2113 | 2" , SCH: SCH.10S | 2" , SCH: SCH.10S | As standard | - | 175 | 5.3 | 19.02~36.9 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2" /300# | 2" /300# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes (Key operated) | Yes (junction box Eexd is included) | Yes
Table 4 | ESDV-2272 | 3" , SCH: 80 | 3" , SCH: 80 | 6 | - | 175 | 5.1 | 37 | 1 | Ball valve | Full bore | Trunnion Mounted | 3" | 3" /300# | 3" /300# | ASTM A105 | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes (Key operated) | Yes (junction box Eexd is included) | Yes
Table 5 | BDV-2110 | 3" , SCH: 160 | 3 , SCH: 160 | 6 | - | 175 | 5.3 ~ 9 | 19 ~ 37.17 | 1 | Ball valve | Full bore | Trunnion Mounted | 3" | 3"/300# | 3"/300# | ASTM A105 | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Open | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Deleted | BDV-2122A | 2" , SCH: 80 | 2" , SCH: 80 | 6 | - | 175 | 4.9 | 18.9 ~ 36.78 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/300# | 2"/300# | ASTM A216 Gr. WCB | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Open | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
| BDV-2122B | 2" , SCH: 80 | 2" , SCH: 80 | 6 | - | 175 | 4.9 | 18.9 ~ 36.78 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/300# | 2"/300# | ASTM A216 Gr. WCB | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Open | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
| BDV-2122C | 2" , SCH: 80 | 2" , SCH: 80 | 6 | - | 175 | 4.9 | 18.9 ~ 36.78 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/300# | 2"/300# | ASTM A216 Gr. WCB | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Open | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 6 | BDV-2134A | 2" , SCH: 80 | 2" , SCH: 80 | 6 | - | 175 | 18.1~ 22 | 22 ~ 59.88 | 1 | Ball valve | Full bore | Floating | 2" | 2" /300# | 2"/300# | ASTM A105 | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Open | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes (Key operated) | No | No
Table 7 | BDV-2134B | 2" , SCH: 80 | 2" , SCH: 80 | 6 | - | 175 | 18.1~ 22 | 22 ~ 59.88 | 1 | Ball valve | Full bore | Floating | 2" | 2" /300# | 2"/300# | ASTM A105 | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Open | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes (Key operated) | No | No
Table 8 | BDV-2134C | 2" , SCH: 80 | 2" , SCH: 80 | 6 | - | 175 | 18.1~ 22 | 22 ~ 59.88 | 1 | Ball valve | Full bore | Floating | 2" | 2" /300# | 2"/300# | ASTM A105 | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Open | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes (Key operated) | No | No
Table 9 | BDV-2132A | 1 1/2" , SCH: 40S | 1 1/2" , SCH: | As standard | - | 175 | 54.1 ~ 62 | 22 ~ 60 | 1 | Ball valve | Full bore | Floating | 1 1/2" | 1 1/2" /600# | 1 1/2" /600# | ASTM A182 GR.F316L | As valve Body | A193 B8 / A194 8 | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Open | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes (Key operated) | No | No
Table 10 | BDV-2132B | 1 1/2" , SCH: 40S | 1 1/2" , SCH: | As standard | - | 175 | 54.1 ~ 62 | 22 ~ 60 | 1 | Ball valve | Full bore | Floating | 1 1/2" | 1 1/2" /600# | 1 1/2" /600# | ASTM A182 GR.F316L | As valve Body | A193 B8 / A194 8 | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Open | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes (Key operated) | No | No
Table 11 | BDV-2132C | 1 1/2" , SCH: 40S | 1 1/2" , SCH: | As standard | - | 175 | 54.1 ~ 62 | 22 ~ 60 | 1 | Ball valve | Full bore | Floating | 1 1/2" | 1 1/2" /600# | 1 1/2" /600# | ASTM A182 GR.F316L | As valve Body | A193 B8 / A194 8 | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Open | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes (Key operated) | No | No
Table 12 | BDV-2141 | 1 1/2" , SCH: 160 | 1 1/2" , SCH: 160 | 3 | - | 175 | 53.9 ~ 62 | 21 ~ 59.89 | 1 | Ball valve | Full bore | Floating | 1 1/2" | 1 1/2" /600# | 1 1/2" /600# | ASTM A105 | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Open | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes (Key operated) | No | No
Table 13 | BDV-2151 | 3" , SCH: 80 | 3" , SCH: 80 | 6 | - | 175 | 52.9 ~ 62 | 22~ 59.4 | 1 | Ball valve | Full bore | Floating | 3" | 3" /600# | 3" /600# | ASTM A105 | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Open | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes (Key operated) | No | No
Table 14 | XV-2112 | 4" , SCH: 40 | 4" , SCH: 40 | 6 | - | 175 | 18.5 | 15.2~ 32.0 | 1 | Ball valve | Full bore | Trunnion Mounted | 4" | 4"/300# | 4"/300# | ASTM A105 | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | No | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes
Table 15 | XV-2121A | 8" , SCH: 60 | 8" , SCH: 60 | 6 | - | 175 | 5.1 | 19.02~ 36.92 | 1 | Ball valve | Full bore | Trunnion Mounted | 8" | 8"/300# | 8"/300# | ASTM A105 | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 9 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 16 | XV-2121B | 8" , SCH: 60 | 8" , SCH: 60 | 6 | - | 175 | 5.1 | 19.02~ 36.92 | 1 | Ball valve | Full bore | Trunnion Mounted | 8" | 8"/300# | 8"/300# | ASTM A105 | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 9 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 17 | XV-2121C | 8" , SCH: 60 | 8" , SCH: 60 | 6 | - | 175 | 5.1 | 19.02~ 36.92 | 1 | Ball valve | Full bore | Trunnion Mounted | 8" | 8"/300# | 8"/300# | ASTM A105 | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 9 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 18 | XV-2122A | 2" , SCH: 10S | 2" , SCH: 10S | As standard | - | 175 | 4.9 | 36.78 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/300# | 2"/300# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | Yes | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 19 | XV-2122B | 2" , SCH: 10S | 2" , SCH: 10S | As standard | - | 175 | 4.9 | 36.78 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/300# | 2"/300# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | Yes | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 20 | XV-2122C | 2" , SCH: 10S | 2" , SCH: 10S | As standard | - | 175 | 4.9 | 36.78 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/300# | 2"/300# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | Yes | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 21 | XV-2123A | 2" , SCH: 160 | 2" , SCH: 160 | 6 | - | 175 | 5.1 | 19.02~ 36.92 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/300# | 2"/300# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | No | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 22 | XV-2123B | 2" , SCH: 160 | 2" , SCH: 160 | 6 | - | 175 | 5.1 | 19.02~ 36.92 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/300# | 2"/300# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | No | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 23 | XV-2123C | 2" , SCH: 160 | 2" , SCH: 160 | 6 | - | 175 | 5.1 | 19.02~ 36.92 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/300# | 2"/300# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | No | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 24 | XV-2124A | 2" , SCH: 40 | 2" , SCH: 40 | 1 | - | 175 | 7.5 | 60 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/300# | 2"/300# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | No | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 25 | XV-2124B | 2" , SCH: 40 | 2" , SCH: 40 | 1 | - | 175 | 7.5 | 60 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/300# | 2"/300# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | No | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 26 | XV-2124C | 2" , SCH: 40 | 2" , SCH: 40 | 1 | - | 175 | 7.5 | 60 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/300# | 2"/300# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | No | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 27 | XV-2131A | 2" , SCH: 10S | 2" , SCH: 10S | As standard | - | 175 | 18.1 | 59.88 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/300# | 2"/300# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 28 | XV-2131B | 2" , SCH: 10S | 2" , SCH: 10S | As standard | - | 175 | 18.1 | 59.88 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/300# | 2"/300# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 29 | XV-2131C | 2" , SCH: 10S | 2" , SCH: 10S | As standard | - | 175 | 18.1 | 59.88 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/300# | 2"/300# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 30 | XV-2133A | 6" , SCH: 40S | 6" , SCH: 40S | As standard | - | 175 | 54.1 | 60 | 1 | Ball valve | Full bore | Trunnion Mounted | 6" | 6"/600# | 6"/600# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 7 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 31 | XV-2133B | 6" , SCH: 40S | 6" , SCH: 40S | As standard | - | 175 | 54.1 | 60 | 1 | Ball valve | Full bore | Trunnion Mounted | 6" | 6"/600# | 6"/600# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 7 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 32 | XV-2133C | 6" , SCH: 40S | 6" , SCH: 40S | As standard | - | 175 | 54.1 | 60 | 1 | Ball valve | Full bore | Trunnion Mounted | 6" | 6"/600# | 6"/600# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 7 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 33 | XV-2134A | 6" , SCH: 40S | 6" , SCH: 40S | As standard | - | 175 | 54.1 | 60 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/600# | 2"/600# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | No | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 34 | XV-2134B | 6" , SCH: 40S | 6" , SCH: 40S | As standard | - | 175 | 54.1 | 60 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/600# | 2"/600# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | No | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 35 | XV-2134C | 6" , SCH: 40S | 6" , SCH: 40S | As standard | - | 175 | 54.1 | 60 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2"/600# | 2"/600# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | No | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 36 | XV-2142 | 6" , SCH: 80 | 6" , SCH: 80 | 3 | - | 175 | 53.9 | 59.89 | 1 | Ball valve | Full bore | Trunnion Mounted | 6" | 6" /600# | 6" /600# | ASTM A105 | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 7 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 37 | XV-2143 | 2" , SCH: 80 | 2" , SCH: | As standard | - | 175 | 53.9 | 59.89 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2" /600# | 2" /600# | ASTM A105 | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 7 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | 0
Table 38 | XV-2144 | 2" , SCH: 40S | 2" , SCH: | As standard | - | 175 | 53.9 | 59.9 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2" /600# | 2" /600# | ASTM A351 GR.CF3M | As valve Body | A193 B8 / A194 8 | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 39 | XV-2271 | 2" , SCH: 160 | 2" , SCH: 160 | 6 | - | 175 | 4.9 | 18.88~ 36.7 | 1 | Ball valve | Full bore | Trunnion Mounted | 2" | 2" /300# | 2" /300# | ASTM A105 | As valve Body | A193 B7 / A194 2H | YES | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Not Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | Yes | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes (Key operated) | No | Yes
Table 40 | XV-2301 | 3" , SCH: 40 | 3" , SCH: 40 | 3 | - | 175 | 1 | AMB | 2 | Ball valve | Full bore | Trunnion Mounted | 3" | 3" /300# | 3" /300# | ASTM A105 | As valve Body | A193 B7 / A194 2H | No | 316 SS | Soft Seat | RPTFE | Anti-Blow Out | 17-4ph | Graphite | spiral wound | Side Entry | Standard | ANSI Class VI | Required | Single Acting , Spring Return | On/Off | MAX/NOR/MIN: 10/7/3 bar-g | Fail to Close | 5 S | Yes | 1/4" NPT | Yes | Yes | N/A | 3 Way | AISI 316 S.S | IP-65 | EEx "d" ,IIB T4 | ISO M20 x 1.5 | Yes | 24 VDC | No | 1/4" NPT | Magnetically operated ‘REED’ contacts | 1 | 24V DC , 1A | Fully Open/Close | Die Cast Aluminum | IP-65 | EEx "d" ,IIB T4 | ISO M20 × 1.5 | Will be specified | Will be specified | Will be specified | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No | No | No | Yes
ESDV’s and associated accessories/equipment’s/cables located in the area where fire could be developed and were indicated in the individual Data Sheets, must be fire resistant for at least 30 minutes at 980°C, as per API 6FA.
The following components shall be fire proofed:
1. Pneumatic actuator
2. Solenoid valves
3. Air filter and lubricator
4. Components of fail‐safe (FS) system
The following components shall not be fire proofed:
1. Body valve (it shall be fire resistant)
2. SS tubing, which is highly resistant to failure during HC fire.
Lifting lugs shall be equipped with valves 3" and higher. Offer shall be revised accordingly.
Rev.04