## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0002 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2525 |  |  | Transmital Date: 12/26/2023
Document Title: LV Switchgear/MCC Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-2525 |  |  | Transmital Date: 12/26/2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-SL-0002_D05 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised and isuued as AFD after finalizing or minor comments on following documents and below mentioned comments: -Electrical Load List -Calculation note for capacitor bank -Electrical Power & Control Cable Schedule Cable size, type and tag shall be added and specified for all incoming and outgoing feeders base on latest cable sizing and cable schedule. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | در هر زمان از پروژه که تغییراتی در لیست بار برق توسط بخش فرآیند به وجود آید، این مدرک به روزرسانی خواهد شد. بعد از نهایی شدن محاسبات کابل، سایز کابل در این مدرک نشان داده می شود. |  |  | Will be checked later.
2 | There is conflict between this document and electrical typical schematic diagrams For LV panel such as Metering&Protection, Switch fuse, etc . (The document need to match) |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | مدرک اسکماتیک و تک خطی هردو به روزرسانی شده و ارسال می گردند. |  |  | Noted and Closed.
3 | Spare feeder shall be considered base on used feeders in single line diagram from point of view size and type. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | فیدرهای Spare اصلاح می گردد. |  |  | See below item 21.
4 | According to our telephone conversation the rated current of main bus bar shall be considered 2000A instead of 1600A (Base on basic single line diagram). |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | بر اساس مدارک پایه به 2000 تغییر پیدا کرد. |  |  | Noted and Closed.
5 | Short circuit time withstand current for diesel generator LV switchgear shall be modified to 1S. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | اعمال گردید |  |  | Noted and Closed.
6 | According to Electrical Systems Design Criteria 27/27R, 50BF shall be considered for incomings and bus tie. Meanwhile it shall be mentioned that when function 27 is activated, all outgoing feeders shall be tripped. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | به وسیله یک نوت اضافه گردید. |  |  | See below item 22.
7 | Status to DCS shall be shown for bus tie, all incomings and outgoing motor type feeders. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | همانطور که در مدرک اسکماتیک نشان داده شده است، تمامی سیگنالهای فیدرهای موتوری توسط IRP به DCS فرستاده می شود و نیز مدارک تک خطی و اسکماتیک در مراجع یکدیگر درج شده اند. همچنین نوت شماره 9 جهت ایجاد ارتباط بین ورودی و کوپلر با سیستم dcs اضافه گردید. |  |  | Noted and Closed.
8 | Electrical Interlock with upstream shall be shown. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | در کنار ترانسهای ورودی، "INTERTRIP FROM 11kV SWGR " و "INTERTRIP TO 11kV SWGR " نشان داده شده است. |  |  | See below item 23.
9 | Size of capacitor banks shall be modified base on comments on Calculation note for capacitor bank (especially NISOC comments.) |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | مطابق با آخرین محاسبات بانک خازنی و بر اساس ترنسمیتال 590، ظرفیت بانک خازنی 120 کیلووار است که در مدرک در نظر گرفته شده است. در صورت هرگونه تغییر در لیست بار و اضافه شدن توان بیشتر، این مدرک مورد بازنگری قرار خواهد گرفت. |  |  | Noted and Closed.
10 | Current and voltage fualt signal lamp shall be considered separately. Meanwhile all signal lamps descriptions shall be added. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | این بند به صورت یک نوت در مدرک اضافه گردید. |  |  | Noted and Closed.
11 | Number of current transformer for capacitor bank shall be specified. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | عدد یک برای CT بانک خازنی اضافه گردید. چراکه این CT برروی فاز وسط قرار میگیرد. |  |  | Noted and Closed.
12 | Voltage sample for capacitor bank shall be shown.Tag of Capacitor bank (A or B) shall be specified too. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | اعمال گردید. |  |  | Noted and Closed.
13 | Emergency stop and start pushbutton shall be considered for all incoming and outgoing feeders on front of switchgear. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | برای فیدرهای خروجی موتوری استارت از طریق LCS و ریموت وجود دارد. در حالیکه STOP از همه جا از جملع درب فیدرامکان پذیر است. برای فیدرهای خروجی غیرموتوری نیز کلید MCCB وجود دارد که استارت و استاپ از طریق چرخش سوییپ نصب شده بر روی درب تابلو مهیا خواهد بود. اسکماتیک استارت و استاپ در مدرک "BK-GCS-PEDCO-120-EL-DG-0002' نشان داده شده است. در مورد فیدرهای ورودی و کوپلر (ACB) نیز نوت 10 اضافه گردید. این نوت در مدرک اسکماتیک نیز اشاره شده است. |  |  | See below item 24.
14 | 400/230V isolating transformer shall be considered separately for each cell. (As sample format) |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | نوت شماره 11 به مدرک اضافه گردید. |  |  | Noted and Closed.
15 | Phase Sequence or Phase Balance Relay (47) shall be added for motor starters 18.5kW and above. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | همانطور که در مدرک اسکماتیک نشان داده شده است، تیپ فیدر M3 که برای موتورهای بالاتر از 18.5 کیلووات می باشد، دارای رلهMPR است. |  |  | See below item 25.
16 | Following items shall be added or modified in SLD: |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09
16-1 | 74TCS and other current protection shall be considered in integrated protection unit and then shall be connected to 86 lock out relay. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | برای تمام ورودیها و کوپلرها در نظر گرفته شد. |  |  | Noted and Closed.
16-2 | Alarm window and related note shall be added. (This note shall be added: Alarm window shall be equiped with acknowledge and reset button.) |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | اعمال گردید. |  |  | Noted and Closed.
16-3 | Type of connection (Hardwire/Serial Link) between measuring unit and DCS shall be shown. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | Serial Link در نظر گرفته شده است. |  |  | Noted and Closed.
16-4 | Selector switch of incomings and bus bars shall be able to show single phase voltage (added as note) |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | به صورت یک نوت اضافه گردید. |  |  | Noted and Closed.
16-5 | According to our agrrement, Switchgear tag shall be added. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | اعمال گردید |  |  | Noted and Closed.
16-6 | Frequency added in measuring unit |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | اعمال گردید |  |  | Noted and Closed.
17 | Feeder category shall be checked and modified in table for example Feeder category for main compressor carn (CR-101) and Fire Water Pumps cran (CR-014) shall be modified to F1. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | فیدربندی خروجی ها بر اساس مدرک لیست بار به روزرسانی گردید. |  |  | Noted and Closed.
18 | NDP-2101B and NDP-2101C on BUSB shall be clarify (Trere are not in load list). |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | فیدربندی خروجی ها بر اساس مدرک لیست بار به روزرسانی گردید. |  |  | Noted and Closed.
19 | According to IPS-M-EL-143, clause 9.6.3: The heaters shall be fed from dedicated power supply. This power supply system may be energized from a dedicated heater panel, independent distribution panel. The panels feeding the heaters in one section of the switchgear shall be fed from the opposite section of the bus bar. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | مطابق با در ردیف 72 از مدرک لیست بار فیدر SPH-01 & SPH-02 برای این منظور در نظر گرفته شده است. |  |  | Noted and Closed.
20 | Complementry comments will be submitted after receive prerequisit and revised document. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | اعمال گردید.. |  |  | Noted and Closed.
21 | Re. item 3 above: The number of 40A Motor spare feeder, type M3 on bus A shall be modified. |  | BK-SUR-ENG-ELE-01-03999 | 2022-04-20 | با توجه به تغییرات تیپ های موتوری، مدرک اصلاح گردید. |  |  | See below item 29.
22 | Re. item 6 above: According to previous comment, 27R shall be considered for incomings and bus tie. |  | BK-SUR-ENG-ELE-01-03999 | 2022-04-20 | اعمال گردید.. |  |  | Noted and Closed.
23 | Re. item 8 above: Electrical Interlock (Mechanical/Electrical) with upstream shall be shown. |  | BK-SUR-ENG-ELE-01-03999 | 2022-04-20 | اعمال گردید.. |  |  | Noted and Closed.
24 | Re. item 13 above: According to our telephone conversation, emergency stop and start (Only for test) pushbutton shall be considered for motor outgoing feeder and MCCB type outgoing feeder equiped with rotary switch (For MCCB type added as note to considered in vendor document.) |  | BK-SUR-ENG-ELE-01-03999 | 2022-04-20 | برای فیدر های موتوری شستی استوپ اضطراری اضافه گردید همچنین rotary switch در نوت 14 اضافه گردید. |  |  | See below item 30.
25 | Re. item 15 above: Phase Sequence or Phase Balance Relay (47) shall be added for motor starters 18.5kW and above. |  | BK-SUR-ENG-ELE-01-03999 | 2022-04-20 | با توجه به تغییرات تیپ های موتوری، مدرک اصلاح گردید. |  |  | See below item 31.
26 | According to our telephone conversation the connection between measuring unit and DCS will be serial link, but on pages 8 and 13 has been considered transducer. It shall be modify. |  | BK-SUR-ENG-ELE-01-03999 | 2022-04-20 | پیرو تماس تلفنی ارتباط سریال لینک و آنالوگ دستگاه اندازه گیری به DCS در نظر گرفته شد. |  |  | Noted and Closed.
27 | According to our telephone conversation, mechanical transformer protections (63,71,26) shall be connected to Seperat lock out relay (Flagged and Locked Send&Receive Relay ) in LV switchgear. |  | BK-SUR-ENG-ELE-01-03999 | 2022-04-20 | اعمال گردید. |  |  | Noted and Closed.
28 | According to our telephone conversation status of DGCB and related incoming LV switchgear shall be modified. (If Required) |  | BK-SUR-ENG-ELE-01-03999 | 2022-04-20 | اعمال گردید. |  |  | Noted and Closed.
29 | Re. item 21 above: Following items shall be rechecked and modified: |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29 | موارد اعمال می گردد. |  |  | Noted and Closed.
29-1 | 8 No. type M3 feeders will be fed by BUS A, but only one spare feeders has been considered on BUS A. |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29 | اضافه گردید. |  |  | Noted and Closed.
29-2 | Slug Pump B on bus B shall be modified to type M4, instead of type M3. Meanhwile in spare feeder electronic overload relay shall be considered instead of direct overload relay. |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29 | با توجه به توافقات صورت گرفته از MPR به جای بی متال الکترونیکی برای فیدرهای تیپ M4 لحاظ گردید. |  |  | Noted and Closed.
29-3 | Feeder 7 on bus B (LP FLARE PACKAGE) is type F2, so ammeter shall be deleted. |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29 | با توجه به کلید 50 آمپر تیپ فیدر به F1 تغییر یافت. |  |  | Noted and Closed.
29-4 | Spare feeder for HVAC PANEL FOR CONTROL ROOM (400A, Type F3) and FIRE WATER JOCKY PUMP (20KW, TYPE 2) shall be added on emergency bus. |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29 | اعمال گردید. |  |  | Noted and Closed.
30 | According to our telephone conversation, in addition to shematic diagram document, emergency stop and start (Only for test) pushbutton shall be shown for motor outgoing feeders. |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29 | مطابق با مدرک اسکماتیک، پوش باتون استارت فقط برای حالت تست و پوش باتتون استاپ قارچی در نظر کرفته شده است |  |  | Noted and Closed.
31 | According to our telephone conversation, base on note 2, Phase Sequence or Phase Balance Relay (47) shall be added for all motor starters 18.5kW and above. |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29 | مطابق با مدرک اسکماتیک اعمال گردید. |  |  | Noted and Closed.
32 | No Comment. Note: According to item 1, if any changes in prerequisit documents such as load list, this document shall be revised. For example according to our telephone conversation CCTV UPS feeder shall be added. Meanwhile base on previous revision and NISOC comment, the voltmeter of emergency incoming in LV switchgear shall be fed from PT in DG local panel. |  | BK-SUR-ENG-ELE-01-05544 | 2022-08-28 | تغییرات در هر مرحله که بر لیست بار مترتب گردد، باعث بروزرسانی این مدرک خواهد شد. |  |  | Will be checked later.
33 | No Comment. Note: following Items shall be checked and modified in next revision. |  | BK-SUR-ENG-ELE-01-07150 | 2023-03-11
33-1 | According to telephone conversation, Spare feeders shall be rechecked and modified base on used feeders for exapmle spare feeders for 30KW and 2.2KW motor feeders and Number of 50A feeder on emergency switchgear shall be rechecked and modified. |  | BK-SUR-ENG-ELE-01-07150 | 2023-03-11 | به روزرسانی شده است. |  |  | See below item 34.
33-2 | According to telephone conversation, Ammeter and 50G shall be added to auxiliary panel for gas compressor on BUS B. |  | BK-SUR-ENG-ELE-01-07150 | 2023-03-11 | تیپ این فیدر غیرموتوری بوده و بر اساس اسکماتیک، F3 می باشد. بر همین اساس به روزرسانی گردید. |  |  | Noted and Closed.
33-3 | According to telephone conversation, this document shall be compatible with electrical load list from point of rated power view such as slug pump and close drain pump feeder. |  | BK-SUR-ENG-ELE-01-07150 | 2023-03-11 | مدرک لیست بار مطابق با آخرین توانهای مصرفی بخش مکانیک در حال به روزرسانی میباشد که نتیجه آن در مدرک لیست کابل با شماره ترنسمیتال 2487 منعکس شده و برای آن کارفرمای محترم ارسال شده است. در حال حاضر لیست بار و لیست کابل تقریبا نهایی می باشد و جهت خرید تابلوهای LV می توان به آن استناد نمود. همچنین تمام تابلوهای LV مورد نیاز شرکت هوایار به مدرک اضافه شده است. با این حال مدرک لیست بار به روزرسانی خواهد شد و ارسال می گردد. در حال حاضر مدرک لیست کابل به روزبوده و ملاک تولید مدارک می باشد. |  |  | See below item 35.
33-4 | CCTV building lighting panel feeder shall be added base on comments on load list. |  | BK-SUR-ENG-ELE-01-07150 | 2023-03-11 | کابل CCTV اضافه گردید. از اینرو فیدر ورودی آن نیز لحاظ شد. |  |  | See below item 36.
34 | See above item 33-1: According to our telephone conversation, the spare feerders shall be rechecked and modified based on used feeders. For example 18.5kw and 30KW spare feeders on BUS A/B shall be modified. |  | BK-SUR-ENG-ELE-02-08938 | 2024-01-10 | اصلاح گردید.
35 | See above item 33-3: According to our telephone conversation, this document shall be compatible with electrical load list and electrical cable schedule for example following items shall be rechecked from point of BUS A/B view. -PK-2201 -PK-2207 -P-2203A/B -P-2202A/B -P-2209 -P-2206 -GCS-400-MCC-01/02 -WS-PR-01 -WS-PR-03 -WS-UT-01 -WS-UT-02 |  | BK-SUR-ENG-ELE-02-08938 | 2024-01-10 | با توجه به جلسات برگزار شده با آن کارفرمای محترم و همچنین تولید ویرایش هشتم از مدرک لیست بار الکتریکی با ترنسمیتال 2764، دیاگرام تک خطی به روزرسانی گردید. لذا حتی المقدور بین مدرک لیست بار و دیاگرام یکسان سازی صورت گرفته است. در صورت تغییر در لیست بار این مدرک مجددا به روزرسانی خواهد شد.
36 | See above item 33-4: Feeder code for Feeder No.22 (CCTV control building) shall be rechecked and modified. |  | BK-SUR-ENG-ELE-02-08938 | 2024-01-10 | اصلاح گردید.
37 | According to our telephone conversation following items shall be rechecked and modified for auxiliary MCC of compressors: |  | BK-SUR-ENG-ELE-02-08938 | 2024-01-10
37-1 | As per Havayar drawings, LCS is not required for each auxiliary load. All auxiliary loads for each compressor will be controlled via dedicated LCP. So LCSs shall be deleted and replaced with one LCP. Also feeder typical diagram M5 shall be modified accordingly. |  | BK-SUR-ENG-ELE-02-08938 | 2024-01-10 | اصلاح گردید.
37-2 | 50G is not required for motors bellow 18.5kW so this relay and related core balance CT shall be deleted based on feeder typical diagram M5. |  | BK-SUR-ENG-ELE-02-08938 | 2024-01-10 | اصلاح گردید.
37-3 | M5 typical description on sheet No.2 shall be modified. (MPR is not required) |  | BK-SUR-ENG-ELE-02-08938 | 2024-01-10 | اصلاح گردید.
37-4 | No. of MCCB pole for F9 feeder in SLD shall be rechecked and modified based on F9 typical diagram. |  | BK-SUR-ENG-ELE-02-08938 | 2024-01-10 | مطابق با مکالمات تلفنی اصلاح گردید.
37-5 | Spare feeders shall be rechecked and modified based on used feeder in SLD. |  | BK-SUR-ENG-ELE-02-08938 | 2024-01-10 | یک عدد فیدر اضافی برای هوایار در نظر گرفته شده است.
38 | Rated power of transformers and rated current of bus bar shall be rechecked and modified after finalizing load list (If required). |  | BK-SUR-ENG-ELE-02-08938 | 2024-01-10 | با توجه به نهایی شدن تقریبی لیست بار، ترانسفورماتور 1250 کیلوولت آمپر کفایت می نماید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: