## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-IN-DG-0005 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2591 |  |  | Transmital Date: 2/21/2024
Document Title: Control System/ESD system Loop Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-2591 |  |  | Transmital Date: 2/21/2024
[5 empty] | CRS No: NISOC-CRS-BK-PPL-PEDCO-320-IN-DG-0005_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در مورد بند 2 R.S، با توجه به ضریب ایمنی ESDV لازم است به نحوی برای کابل سلونوئید ولو spare در نظر گرفته شود. پیمانکار در این زمینه راهکار خود را ارائه نماید. |  | 1402-2294-536276 | 1402/12/23 | از آنجایی که Valve 3202 ، در واحد PPL منطق و Interlock ساده ای دارد و فقط با سلکتور و/یا EMERGENCY STOP PUSH BUTTON (MUSHROOM HEAD KEY LATCH TYPE) تغییر وضعیت می دهد، در عمل دو فرمان بر روی یک ON-Off Valve داریم که بصورت موازی، عملکرد یکدیگر را همراهی می کنند. از طرفی: فرمان ESOV از آنجایی که فرمان Emergency Shutdown هست، مدار فرمان آن به صورت Fail Safe تعریف و بسته می شود. بنابراین در صورت بروز خطای احتمالی (قطعی کابل، هوای ابزار دقیق ...) شیر به سمت حالت امن: Close می رود، بنابراین برای ضریب ایمنی ESDV مشکلی وجود نخواهد داشت.(‌با توجه به مدار موجود دوکابله کردن کمکی به افزایش سیستم ایمنی نکرده و توصیه نمیشود)
2 | بدیهی است که مسئولیت تطابق مدارک اصلاحی با نقطه نظرات کارفرما و همچنین صحت و کفایت محتوای کلیه مدارک ارسالی مطابق شرح خدمات و استانداردهای تصریح شده در اسناد مناقصه، استانداردهای IPS و دیگر مدارک پروژه بر عهده پیمانکار بوده و نقطه نظرات کارفرما رافع مسئولیت پیمانکار نمی باشد. |  | 1402-2294-536276 | 1402/12/23 | ملاحظه شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: