## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-TB-0003 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2728 |  |  | Transmital Date: 7/22/2024
Document Title: TBE For Existent MV Switchgear Expansion, RCP & MV Capacitor Bank |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-2728 |  |  | Transmital Date: 7/22/2024
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-TB-0003_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Following items shall be added to TCL and completed by vendor in next revision: |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 |  |  |  | Item 8 below.
1-1 | Certificate or license, test reports and type test shall be submitted based on latest revison of related standard especially for MV switchgear such as IP, short circuit level, temperature rise and etc. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید. |  |  | Item 9 below.
1-2 | Vendor is supposed to prepare preliminary substation arrangement drawing for this project and consider dummy panel (if required). See and use attached file as project arrangement document. It is obvious exact number of dummy panels will be specified by vendor. Meanwhile dummy panel(s) shall be similar to other cubicles. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردید. |  |  | Noted and Closed.
1-3 | Exact part list of the Switchgear including equipment name, brand, model and origin shall be submitted considering this TCL. Vendor is responsible for exact part list of the SWG. If any item to be missed from the part list, Vendor shall consider it without any cost & time impact. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | بند 28 به TCL اضافه گردید. |  |  | Noted and Closed.
1-4 | Native completed deviation from Purchase Order or Purchaser procurement documents shall be submitted in next revision. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردید. |  |  | Noted and Closed.
1-5 | All required signals and mapping shall be submitted and considered From/To DCS base on "Electrical I/O Signal List BK-GCS-PEDCO-120-EL-LI-0005". Manufacturer shall consider suitable relays / auxiliary contacts for this reason. Vendor shall confirm necessary facility will be considered. Please follow Electrical I/O Signal List (See attach file). |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | بند 29 به TCL اضافه گردید. |  |  | Noted and Closed.
1-6 | Certificate for country of origin shall be submitted by Vendor (after PO.). Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | بند 26 از TCL اصلاح گردید.
1-7 | Burden of CT’ & PT’s will be finalized after purchase order based on the related calculation that will be submitted by Vendor and shall be approved by Purchaser. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردیید. |  |  | Noted and Closed.
1-8 | The software of the protection relay shall be provided with original licence. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردیید. |  |  | Noted and Closed.
1-9 | All protection relays are equipped with key pan and LCD display, and 7 Numbers Digital input /7 Numbers Dry Output Contacts as minimum which is should be re-checked with schematic diagram. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | بند 32 از TCL اضافه گردید. |  |  | Noted and Closed.
1-10 | All relays supplied with MV switchgear shall be microprocessor based, which will facilitate a connection to DCS. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید. |  |  | Noted and Closed.
1-11 | Vendor shall perform programming of the relays based on requirements of logic diagram. Related documents shall be submitted. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید. |  |  | Noted and Closed.
1-12 | Vendor shall perform relay setting and relay coordination based on project relay coordination and setting study. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید. |  |  | Noted and Closed.
1-13 | All digital multimeters and protection relays shall have Mod Bus (RS 485) communication protocol. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید. |  |  | Noted and Closed.
2 | Following description shall be added to Item 1 in TCL: Vendor shall submitted temperature de‐rating factors of equipment such as CB, etc. It means Vendor shall de-rate the rated current of equipment on the site condition such way that de-rated rated current be equal or higher than rate current. De-rating curves/Tables (altitude & Ambient Temperature) shall be submitted at this stage. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید. |  |  | Noted and Closed.
3 | Following description shall be added to Item 7 in TCL: Sub vendor list shall be submitted and following items shall be specified in sub vendor list: -Manufacture -Country of origin -Model Consideration shall be given that |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردید. |  |  | Noted and Closed.
4 | Item 8 in TCL shall be modified as below: Based on the 22-E&C-QC-SP-1,Spare parts for pre-commissioning, commissioning/start up and spare parts for two years shall be submitted separately based on Spare Parts Specification. The supplied spare parts shall comply with the same specifications as the original parts and shall be interchangeable with the original parts without any modification. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید. |  |  | Noted and Closed.
5 | Item 18 in TCL shall be modified as below: All the following items shall be considered in proposal for all Vacuum Circuit Breakers: Anti-pumping device, Mechanical operations counter, Manual mechanical trip facility Closed/open position indication, Start/Stop & Emergency Stop push button, Charged/discharged spring indication, Emergency shutdown interposing relay and Minimum 4 numbers make contacts. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردید. |  |  | Noted and Closed.
6 | All manufacturers shall be considered based on MOP. Any deviation from MOP is not acceptable. For example it shall be checked for Petro Tajhiz Iliya. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | شرکت ایلیاتجهیز حذف گردید. |  |  | Noted and Closed.
7 | Complimentary comments will be submitted after submitting revised technical offer based on comments. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | در صورت وجود کامنت های دیگر، این کامنتها در نظر گرفته خواهد شد. |  |  | Noted and Closed.
8 | Item 1 above: TCL shall be filled by vendor and submitted in next technical offer. Moreover, all mentioned documents in TCL shall be submitted by vendor. Otherwise, it will not be acceptable. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
9 | Item 1-1 above: Not accepted. It has not been implemented correctly in TCL by consultant. Related certificate, license, type test and test reports are necessary to submit by vendor at the bid stage to check the quality and capability of vendor. It is very strange that the vendors has not submitted above mentioned documents while has been accepted in TBA by consultant. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
10 | All attached document to MR shall be signed, stamped and submitted by vendor at this stage such as Existent MV Switchgear Expansion Single Line Diagram, Electrical I/O Signal List, Electrical Equipment Arrangement Layout for Building, etc. for example Pars Tableau has not submitted above mentioned documents. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
11 | Technical offer shall be submitted completely for example 3.3KV switchgear, MV capacitor bank and RCP has not been submitted by Pars Tableau. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
12 | All data sheet shall be filled completely by vendor correctly and submitted. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
13 | All deviations shall be filled in native deviation list by vendor (According to TCL) and shall be clarified between consultant and vendor. Then, the results shall be reflected into TBA conclusion. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
14 | All catalogues of electrical equipment such as ACB, protection relay, capacitor bank, etc. shall be submitted by vendor. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
15 | Capacitor bank single line diagram shall be signed and stamped by vendors. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
16 | Guarantee period shall be added to TBE table. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
17 | Due to new MV switchgear cells to be installed in the existing switchgear building and there are limitation in free space, all Bidders to be issued their preliminary arrangement layout including proposed cells dimensions in order to checking installation ability in the available free space. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
18 | Pars Tablo: |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
18-1 | As per MR "which ever comes earlier" phrase shall be deleted from guarantee period in the Pars Tablo technical offer page 5. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Not Acceptable, see item 21 bellow
18-2 | Cell width in the Pars Tablo offer is 900mm but existing cells width is 750mm and equipment arrangement document (BK-GCS-PEDCO-120-EL-PY-0008_D03 ) prepared based on 750mm width for new cells. This item need to check by Consultant due to lack of required space in the switchgear building |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
18-3 | Cell depth in the Pars Tablo offer is 2225mm while existing cells depth is 2000mm. and equipment arrangement document (BK-GCS-PEDCO-120-EL-PY-0008_D03 ) prepared based on 2000mm depth for new cells. This item need to check by Consultant due to lack of required space in the switchgear building |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
18-4 | Capacitor bank, RCP and 3.3kV cell not exist in the Pars Tablo technical offer, how Hirgan did the TBE without technical offer? |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
18-5 | lockout relay 86T has not been considered in the Pars Tablo offer for JT01, 02,03,04. this item to be clarified with the Bidder. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
18-6 | Capacitor bank single line diagram missed from MR attachments. This document shall be send to the Bidders. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
19 | Runin Sanat: |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
19-1 | Proposed lockout relay 94 instead of 86T will be acceptable in case of relay 94 has manual reset capability. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
19-2 | Runin Sanat proposed two cells for 3.3kV switchgear, but in the switchgear equipment arrangement layout, only one cell has been considered. it shall be checked for possibility for layout arrangement. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
19-3 | proposed cells dimensions (HeightxWidthxDepth) shall be specified in the technical proposal. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
19-4 | Proposed IP41 can be acceptable only in case of NISOC approval. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Not Acceptable, see item 22 bellow
20 | Taban Tablo: |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
20-1 | Proposed IP41 can be acceptable only in case of NISOC approval. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Not Acceptable, see item 22 bellow
20-2 | Taban Tablo proposed two cells for 3.3kV switchgear, but in the switchgear equipment arrangement layout, only one cell has been considered. it shall be checked for possibility for layout arrangement. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
20-3 | As per latest capacitor bank single line diagram (TR-2325) MV circuit breaker or load break switch is not required for capacitor bank. Proposal shall be modified. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
20-4 | Regarding latest revision of RCP wiring diagram (Tr-2056) required Start/Stop pushout is 10Nos but in the Taban Tablo technical proposal it has been considered 6 Nos. for each. This item to be clarified and modified based on latest revision of engineering documents. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Noted and Closed.
20-5 | proposed cells dimensions (HeightxWidthxDepth) shall be specified in the technical proposal. |  | BK-SUR-ENG-ELE-02-09120 | 2024-03-13 | مطابق با صورتجلسه مورخ 31 اردیبهشت و به نحو مقتضی اعمال شده است. |  |  | Not Acceptable, see item 23 bellow
21 | پاسخ ارائه شده در بند 18-1 بالا مورد پذيرش نيست چراكه در خصوص شرايط گارانتي مطلبي در صورت جلسه آورده نشده است. شرايط گارانتي صراحتا در مدرك MR قيد شده و سازندگان در صورت وجود انحراف از درخواست، موضوع را بايستي در deviation list ذكر نمايند. |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | شرایط گارانتی مطابق MR توسط هر سه وندور پذیرفته شده است و هیچ گونه مغایرتی اعلام نگردیده است
22 | پاسخ ارائه شده در بند هاي 19-4 و 20-1 بالا مورد پذيرش نيست چراكه در خصوص درجه حفاظت IP در صورت جلسه مطلبي آورده نشده است. درجه حفاظت IP42 صراحتا در مدرك Data sheet قيد شده و سازندگان در صورت وجود انحراف از درخواست، موضوع را بايستي در deviation list ذكر نمايند. |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | تابان تابلو و رانین صنعت نمی توانند IP42 را تامین نمایید اما پارس تابلو IP42 را می تواند تامین نمایید . لذا این موضوع در نتیجه گیری TBE آورده شده است .
23 | پاسخ ارائه شده در بند 5-20 بالا مورد پذيرش نيست. ابعاد تابلوهاي پيشنهادي تابان تابلو در پيشنهاد اين شركت وجود ندارد. |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | جانمایی و ابعاد تابلو توسط شرکت تابان تابلو ارائه گردید
24 | با توجه به موارد ذيل و تناقض در پيشنهادات فني سازندگان، مقتضي است جلسه شفاف سازي با سازندگان جهت همسنگ سازي موارد ذيل برگزار گردد: |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | جلسه برگزار گردید
24-1 | جانمايي تابلوهاي جديد (اعم از 11 و 3.3 كيلوولت) جهت مشخص شدن فضاي آزاد در دسترس در ساختمان سوئيچگير موجود مطابق با آخرين نسخه مدرك معماري ساختمان مذكور و همچنين نقشه جانمايي تجهيزات برقي. |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | مدرک جانمایی بعد از عقد قرارداد با وندور منتخب و براساس پیشنهاد ایشان بروز رسانی خواهد شد
24-2 | پيشنهاد فني مربوط به بانك خازني فشار متوسط ميبايست مطابق با آخرين مدرك محاسبات و تك خطي بانك خازني فشار متوسط (350KVAR) ميبايست اصلاح گردد. |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | براساس آخرین مدرک محاسبات بانک خازنی ظرفیت خازنی به 530KVAR تغییر نموده است و وندروهای در مدارک مورد نظر اعلام نموده اند
24-3 | دريافت گواهينامه هاي مربوط به تابلو اعم از تايپ تست (شامل IP، اتصال كوتاه و ...) و همچنين لايسنس در صورت وجود. |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | مدارک فوق توسط برخی از وندورها ارائه شده است و وندروهای دیگر بعد از عقد قرارداد توسط ایشان ارائه خواهد شد
24-4 | ملاك پيشنهاد فني براي RCP، نقشه وايرينگ دياگرام و ديتا شيت آن ميباشد و اقلام مورد نياز براي آن (شامل پوش باتن، چراغ سيگنال و ... ) ميبايست متناسب با مدارك مذكور تهيه گردد. |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | مدرک MR و موارد مذکور توسط وندروها ممهور و امضاء شده است
24-5 | تكميل به همراه مهر و امضاء فرم TCL و همچنين Deviation List (حتي در صورت عدم وجود Deviation) تكميل شده توسط سازندگان. توضيح اينكه در خصوص انحرافات در جلسه مذكور تصميم گيري لازم به عمل خواهد آمد. |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | هر سه وندور ارائه نموده است
24-6 | با توجه به عدم نمايش ترانس جريان يك به يك در نقشه دياگرام تگ خط تابلوي 3.3 كيلوولت پمپ آتش نشاني براي تغذيه آمپرمتر روي LCS بايستي در جلسه به سازندگان يادآوري شود اين CT را در پيشنهاد خود ببينند. |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | نقشه تکخطی با شماره ترنسمیتال ارسالی 2750 بروز رسانی گردیده است و در اختیار تمامی وندورها می باشد
24-7 | مطابق درخواست كارفرما و همانطور كه در نقشه SLD نمايش داده شده براي فيدرهاي 11kV ترانسي و نيز فيدر 3.3kV پمپ آتش نشاني بايستي دو عدد رله 86 (86 و 86T) در نظر گرفته شود در حالي كه پارس تابلو يك عدد رله در نظر گرفته است. لازم است به پيشنهاد اين شركت يك عدد رله 86T يا يك عدد Trip relay 94 اضافه گردد. |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | نقشه تکخطی با شماره ترنسمیتال ارسالی 2750 بروز رسانی گردیده است و در اختیار تمامی وندورها می باشد
24-8 | يك دستگاه VCB Truck بايستي به ليست اقلام Special tools در پيشنهاد پارس تابلو اضافه گردد |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | شرکت پارس تابلو مطابق با صورت جلسه مورخ 1403/06/17 لحاظ نموده است .
24-9 | با توجه به اينكه سازنده موتور اصلي كمپرسورها ترانس جريان از نوع 100/1 , 5P20, 15VA بر روي موتورهاي نصب كرده لذا براي هر فيدر موتوري در تابلوي 11 كيلو ولت سه عدد از همين ترانس جريان براي اعمال حفاظت ديفرانسيل بايستي در نظر گرفته شود. در حال حاضر شركت پارس تابلو مطابق مدرك SLD ترانس كلاس X پيشنهاد داده است. |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | نقشه تکخطی با شماره ترنسمیتال ارسالی 2750 بروز رسانی گردیده است و در اختیار تمامی وندورها می باشد
24-10 | در پيشنهاد فني پارس تابلو براي بانكهاي خازني Inrush current reactor نشان داده شده در مدرك SLD آورده نشده است. براي هر بانك خازني سه عدد از اين تجهيز بايستي به پيشنهاد اضافه شود. |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | شرکت پارس تابلو مطابق با صورت جلسه مورخ 1403/06/17 لحاظ نموده است .
24-11 | لوازم يدكي پيشنهادي توسط رانين صنعت ناقص است لازم است مطابق با پيشنهاد پارس تابلو تكميل شود. |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | لوازم يدكي پيشنهادي توسط رانين صنعت بروزرسانی گردیده است
24-12 | ليست لوازم يدكي در پيشنهاد تابان تابلو ديده نشده است و بايستي اضافه گردد |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | لوازم يدكي پيشنهادي توسط تابان تابلو بروزرسانی گردیده است
25 | با توجه به توافقات صورت پذيرفته در خصوص به روز رساني مدرك تك خطي تابلو فشار متوسط (بند 2 صورتجلسه مورخ 1402/02/31 و همچنين نياز به اصلاح ظرفيت 600 كيلووار بانك خازني قيد شده در اين مدرك)، مقتضي است قبل از به روز رساني مجدد TBE ابتدا مدرك تك خطي به روز رساني و ارسال گردد. |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | نقشه تکخطی با شماره ترنسمیتال 2750 ارائه گردیده است
26 | با توجه به اصلاح عنوان مدرك TBE، مقتضي است مدرك تك خطي تابلو بانك خازني فشار متوسط نيز به مدرك MR اضافه گردد. |  | BK-SUR-ENG-ELE-03-09428 | 2024-07-31 | لحاظ گردید
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: