## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DC CHARGER
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 12
9184 – 073 - 053 |  |  |  | BK |  | GCS | PEDCO | 120 |  | EL | DT | 0002 | D04
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR DC CHARGER نگهداشت و افزایش تولید میدان نفتی بینک
D04 |  |  | Oct.2024 |  | AFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Sadeghian
D03 |  |  | May.2023 |  | AFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | A.M.Mohseni
D02 |  |  | Aug.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D01 |  |  | Jan.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D00 |  |  | Dec.2021 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | Client Approval
Class: | 1 |  |  |  | Client Doc. Number: F0Z-709019
status: |  | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for Client Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DC CHARGER
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 12
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | EL | DT | 0002 |  | D04
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  | X |  | 51
2 | X | X | X |  | X |  | X |  | 52
3 | X | X | X | [5 empty] | 53
4 | X | X | X | [5 empty] | 54
5 | X | X | X | [5 empty] | 55
6 | X | X | [6 empty] | 56
7 | X | X | [6 empty] | 57
8 | X | X | X |  | X |  | X |  | 58
9 |  | X | X | [5 empty] | 59
10 |  | X | X |  | X |  | X |  | 60
11 |  | X | [6 empty] | 61
12 |  | X | [6 empty] | 62
13 | [8 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## 110 VDC.
Technical Data For Industrial Battery & Battery Charger for 110 VDC
Item | Description | Required | Vendor Data
1-General
1.1 | Name of Project / Plant | Binak Oilfield in Bushehr Province
1.2 | Manufacturer | By Vendor
1.3 | Manufacturer Model | By Vendor
1.4 | Average Ambient Temperature (Min/Max) | Min ~ Max: +5 ~ +52°C
1.5 | Max.Design Temperature: | 52 °c
1.6 | Max. Sun Temperature: | + 85 °c
1.7 | Max.Relative Humidity: | 100%
1.8 | Mean Sea Level: | 12.5 m above Sea Level
1.9 | Seismic Factor: | 0.3g
1.10 | Max. Wind Velocity(Max) | 120 km/hr
1.12 | Standard(s) | IEC,IPS-M-EL-174(2), IPS-E-EL-100(1)
1.13 | Quantity | 1 Complete set (2×100% Charger) with commissioning and two years Spare Parts, Two battery bank(2×92cell), Battery Stand with special tools for Batteries, switch-fuse For Battery Banks: Exd IIC-T3 type.
1.14 | Service | 110 VDC for LV & MV Switchgear
1.15 | Tag Number | GCS-110-CHG-001 & GCS-110-CHG-002
1.16 | Applicable SLD | BK-GCS-PEDCO-120-EL-SL-0006
1.17 | Applicable Specification | BK-GNRAL-PEDCO-000-EL-SP-0005
1.18 | Location | Indoor
2-Environment
2.1 | Area classification | Safe Area
2.2 | Site Elevation | 12.5 m |  | AFC
2.3 | Ambient Temperature | Min/Max: +5/52°C |  | AFC
2.4 | Relative Humidity | 100%
2.5 | Atmosphere | Tropical & Dusty
2.6 | Building Temperature Control | Not Required
2.7 | Seismic Acceleration | 0.3g
3.AC Input
3.1 | Rectifiers Input Voltage | 380/400/440v, 3-Ph , 4 wire , 50 Hz
3.2 | Max.allowable input voltage variation | ±10%
3.3 | Max.allowable input frequency variation | ±5%
3.4 | Network short circuit current (rms) | 50KA
3.5 | Network short circuit current (Peak) | By Vendor
3.6 | Max. short circuit clearing time | 1 sec
3.7 | Max. power consumption | By Vendor
3.8 | Input THDi% ( acc to IEEE-519 ) | <10%
4.DC Output
4.1 | Rated voltage | 110 VDC
4.2 | Max. Allowable Voltage Variation | ±1%
4.3 | Rated Output Current (Amp) | 168 Amp
4.4 | Allowable Ripple voltage (r.m.s ) | <1%
4.5 | Overall Efficiency | >90%
4.6 | Rectifier control voltage (Full Control) | 12 Pulse
4.7 | Charger Topology | Parallel
4.8 | Rectifier Input Filter type | R.F.I & Surge Arrester
4.9 | Constant Voltage Control | Required
4.10 | Constant Current Control | Required
4.11 | Rectifier Over Load (%) | 110% Continues
4.12 | Rectifiers Protection | Required
4.13 | MCCB for AC Inputs | Required
4.14 | MCCB for DC Output | Required
4.15 | Ultra Fast Fuse to Protect Thrusters | Required
4.16 | Charger Output Fuse | Required
4.17 | AC Input Voltmeter | Required
4.18 | AC Input Ammeter | Required
4.19 | Charger DC Voltmeter | Required
4.20 | Charger DC Ammeter | Required
4.21 | Charger DC LC Filter | Required
4.22 | Load Current Ammeter | Required
4.23 | Charger Selector Switch | Required
4.24 | Battery Low DC Alarm (Indicator & Dry Contact) | Required
4.25 | Load Low DC Alarm (Indicator & Dry Contact) | Required
4.26 | Load Hi DC Alarm (Indicator & Dry Contact) | Required
4.27 | Batteries Disconnected (Indicator) | Required
5.Battery Charger Cabinet
5.1 | Type | Flat face
5.2 | Construction | Floor Mounted, Free Standing
5.3 | Ingress protection class | IP42
5.4 | Access for maintenance | Front
5.5 | Body material | Carbon Steel Sheet
5.6 | Thickness of body material | Min.2 mm
5.7 | Finish color | RAL 7032
5.8 | Cable entrance | Bottom and Cable Gland
5.9 | Bottom closing method | By Vendor
5.10 | Cooling method | Natural
5.11 | Space Heater | Required
5.12 | Illumination | Required
5.13 | Noise Level | 60dBA
5.14 | Wiring | Power and Control Min.2.5mm², Metering Min.1.5mm²
5.15 | Nameplate | English Black in White Background
5.16 | Earthling System | IT
Note1: Data shown are typical; manufacturer shall provide his own data
Note2: The blank items shall be filled by battery manufacture
6.Batteries
6.1 | Manufacturer | By Vendor
6.2 | Manufacturer Model | By Vendor
6.3 | Standard | IEC 60623, IEEE 1115 2014
6.4 | Quantity | 1 Complete set (2×50% Battery Bank)
6.5 | Service | 110 VDC for LV & MV Switchgear
6.6 | Applicable Specification | BK-GNRAL-PEDCO-000-EL-SP-0005
6.7 | Location | Indoor
6.8 | Battery requirements | By Vendor
6.9 | Battery type | Nickel-Cadmium (IEC60623)
6.10 | Battery charging method | Constant Voltage-Dual Rate and Current Limit with Float/Auto/Equalize/Initial Mode charging
6.11 | Back-up time | 8 Hr
6.12 | Emergency Mode Voltage for each cell (Activated by Battery Room Fan Failure) | 1.35 V ± 0.01 V
6.13 | Battery float charging voltage | 1.42 V/Cell
6.14 | Battery Equalize charging voltage ( 0-30Hr Timer and Reset Push Button are required) | 1.47/Cell
6.15 | Battery boost charging voltage ( 0-30Hr Timer and Reset Push Button are required) | 1.55~1.65 V/Cell
6.16 | Battery initial charging voltage ( 0-30Hr Timer and Returnable Switch are required) | 1.75 V/Cell
6.17 | Battery nominal voltage | 1.2 V/Cell
6.18 | Final discharge voltage per cell(V) | 1.14 V/Cell
6.19 | Rated capacity of each cell at 20 ⁰C | Min 325 Ah
6.20 | Re-charging time to 90% Rated Capacity | 8 Hours
6.21 | Required battery ampere-hour (C5) | 325Ah , SBLE Type
6.22 | Total quantity of cells | 184
6.23 | No. of battery banks | 2
6.24 | No. of batteries per each bank | 92
6.25 | Battery cell dimension (W × D × H ) | By Vendor
6.26 | Battery cell weight | By Vendor
6.27 | Batteries shall be performed from SAFT,ALCAD Batteries | Required
6.28 | All type of Batteries and Battery accessories shall be original and approved by Iranian representative | Required
6.29 | Rate of H2 production during charging | Liter/Cell
6.30 | Required air volume of exchange in battery room | m3/Hours
6.31 | Required air volume of electrolyte | By Vendor
6.32 | Composition of electrolyte | By Vendor
6.33 | Required volume of electrolyte | Liter
6.34 | Required Max. charging current | By Vendor
7.Data sheet for Battery
7.1 | Battery Discharging Rate | Medium Rate
7.2 | Container | Plastic
7.3 | Construction | Vented
8.Accessories & Special Tools
8.1 | Thermometer | Required
8.2 | Hydrometer | Required
8.3 | Voltmeter | Required
8.4 | Battery Racks | Required (Seismic Factor:0.3g)
8.5 | Flame Arrester | Required
8.6 | Stand Type | By Vendor
Note1:Data shown are typical
Note2:The blank items shall be filled by battery manufacture
9.Load Profile Graph
9.1 | T1 :1 Min
9.2 | I1 :5090 W
9.3 | T2 : 7Hr , 58 Min
9.4 | I2 : 2090 W
9.5 | T3 : 1 Min
9.6 | I3 : 6890 W
9.7 | T4 : 1 Min
9.8 | I4 : 5090 W
10.Data Sheet for Distribution Board
10.1 | Standard | IEC,IPS-M-EL-174(2), IPS-E-EL-100(1)
10.2 | Quantity | 1 Complete set
10.3 | Service | DC Distribution Panel
11.Mechanical specification
11.1 | Mounting type | Floor Mounted, Free Standing
11.2 | Body martial | Carbon Steel Sheet
11.3 | Thickness | Min.2 mm
11.4 | Access for maintenance | Front
11.5 | Protection class | IP42
11.6 | Illumination | Required
11.7 | Space heater | Required
11.8 | Weight | By Vendor
11.9 | Dimensions | By Vendor
11.10 | Name plate | English Black in White Background
11.12 | Finished color | RAL 7032
12.Electrical Specification
12.1 | Rated incoming voltage | 110 VDC
12.2 | Rated insulation voltage | By Vendor
12.3 | Wiring | Power and Control Min.2.5mm²,Metering Min.1.5mm²,
13.Incoming
13.1 | Incoming Cables Size & Tag no. | BK-GCS-PEDCO-120-EL-SL-0006
13.2 | Entry Side | Bottom by Cable Gland
13.3 | Cable Entry | Via Removable Gland Plate
13.4 | Incoming Circuit breaker | MCCB
14.3 | Terminal Type and quantity | By Vendor
13.5 | Circuit breaker construction | Fix
14.Outgoing
14.1 | Outgoing cable size and tag no. | BK-GCS-PEDCO-120-EL-SL-0006
14.2 | Entry side | Bottom by Cable Gland
15.Data Sheet for Distribution Board
15.1 | Cable entry | Via Removable Gland Plate
15.2 | Outgoing circuit breaker | MCCB
15.3 | Circuit breaker constructor | Fix
16.Indicating lights , Alarms and Accessories
16.1 | Battery Low DC alarm | Required ,With Dry Contacts
16.2 | Load Low DC alarm | Required ,With Dry Contacts
16.3 | Load Hi DC alarm | Required ,With Dry Contacts
16.4 | Batteries disconnected | Required
16.5 | Battery voltmeter | Required
16.6 | Battery ammeter | Required
16.7 | Load voltmeter | Required
16.8 | Load ammeter | Required
16.9 | Cable gland | Required
16.10 | Removable gland plate | Required
17.Tests ( Factory Acceptance test and Site Acceptance Test shall be performed By the Vendor )
17.1 | Visual Inspection & Dimensional Check | Required
17.2 | Performance and Function Test | Required
17.3 | Sequence , Operation and Logic Test | Required
17.4 | Dielectric Strength Test | Required
17.5 | Output Voltage and Ripple Check | Required
17.6 | Charger Voltage Adjustment Test | Required
17.7 | THDi% Check | Required
17.8 | Output Regulation / Adjustments Test | Required
17.9 | Alarms Check | Required
17.10 | Autonomy Test | Required
17.11 | Current Limit Test | Required
17.12 | Short Circuit test | Required
17.13 | Other Tests shall be performed in Accordance with IEC60146 (Battery Charger Testing) | Required
17.14 | Hardware and Software for Communication, Programming or Setting up the CPU or MPU Boards (If Required), | Required
18.Accessories And Special Tools
18.1 | MIMIC Panel With LED To Show Operation Condition (shall be finalized by vendor) . | Required
18.2 | Commissioning and two years spare parts shall be provided | Required
18.3 | The Accuracy of all meters shall be better than 1.5% | Required
18.4 | On load break switch-fuse For Battery Banks:Exd type IIC-T3 | Required
18.5 | Training | The Supplier /Vendor shall be assumed the maintenance and repair training course at least for 5 People
18.6 | Battery Room Fan failure (Activated by external Signal ) | Required
19.Electromagnetic Compatibility (EMC)
NOTE: 1. All DC-UPS units shall comply with the requirements for EMC as defined in IEC 62040-2, in order to ensure:Conducted emissions in both, the power supply input and output of the DC- UPS are controlled within acceptable limits;Any electromagnetic disturbance generated by the UPS and its individual components do not exceed a level which would affect the correct operation of both, radio and telecommunications equipment;The DC-UPS has an adequate level of intrinsic immunity to external electromagnetic- and conducted disturbance to enable it to operate as intended. 2. A serial link communication protocol shall be considered for sending alarms and indications to DCS by vendor.
تسهیلات
DATA SHEETS FOR DC CHARGER
NISOC
شماره پیمان:
9184 – 073 - 053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
EL
DT
0002
D04
بسته کاری
GCS
پروژه
BK

## 24 VDC
Technical Data For Industrial Battery & Battery Charger for 24 VDC
Item | Description | Required | Vendor Data
1-General
1.1 | Name of Project / Plant | Binak Oilfield in Bushehr Province
1.2 | Manufacturer | By Vendor
1.3 | Manufacturer Model | By Vendor
1.4 | Average Ambient Temperature (Min/Max) | Min ~ Max: +5 ~ +52°C
1.5 | Max.Design Temperature: | 52 °c
1.6 | Max. Sun Temperature: | + 85 °c
1.7 | Max.Relative Humidity: | 100%
1.8 | Mean Sea Level: | 12.5 m above Sea Level
1.9 | Seismic Factor: | 0.3g
1.10 | Max. Wind Velocity(Max) | 120 km/hr
1.12 | Standard(s) | IEC,IPS-M-EL-174(2), IPS-E-EL-100(1)
1.13 | Quantity | 1 Complete set (2×100% Charger) with commissioning and two years Spare Parts, Two battery bank(2×20cell), Battery Stand with special tools for Batteries, switch-fuse For Battery Banks: Exd IIC-T3 type.
1.14 | Service | 24 VDC for F&G System
1.15 | Tag Number | GCS-24-CHG-001 & GCS-24-CHG-002
1.16 | Applicable SLD | BK-GCS-PEDCO-120-EL-SL-0006
1.17 | Applicable Specification | BK-GNRAL-PEDCO-000-EL-SP-0005
1.18 | Location | Indoor
2-Environment
2.1 | Area classification | Safe Area
2.2 | Site Elevation | 12.5 m |  | AFC
2.3 | Ambient Temperature | Min/Max: +5/52°C |  | AFC
2.4 | Relative humidity | 100%
2.5 | Atmosphere | Tropical & Dusty
2.6 | Building Temperature Control | Not Required
2.7 | Seismic Acceleration | 0.3g
3.AC Input
3.1 | Rectifiers Input Voltage | 380/400/440v, 3-Ph , 4 wire , 50 Hz
3.2 | Max.allowable input voltage variation | ±10%
3.3 | Max.allowable input frequency variation | ±5%
3.4 | Network short circuit current (rms) | 50KA
3.5 | Network short circuit current (Peak) | By Vendor
3.6 | Max. short circuit clearing time | 1 sec
3.7 | Max. power consumption | By Vendor
3.8 | Input THDi% ( acc to IEEE-519 ) | <10%
4.DC Output
4.1 | Rated voltage | 24 VDC
4.2 | Max. Allowable Voltage Variation | ±1%
4.3 | Rated Output Current (Amp) | 636 Amp
4.4 | Allowable Ripple voltage (r.m.s ) | <1%
4.5 | Overall Efficiency | >90%
4.6 | Rectifier control voltage (Full Control) | 12 Pulse
4.7 | Charger Topology | Parallel
4.8 | Rectifier Input Filter type | R.F.I & Surge Arrester
4.9 | Constant Voltage Control | Required
4.10 | Constant Current Control | Required
4.11 | Rectifier Over Load (%) | 110% Continues
4.12 | Rectifiers Protection | Required
4.13 | MCCB for AC Inputs | Required
4.14 | MCCB for DC Output | Required
4.15 | Ultra Fast Fuse to Protect Thrusters | Required
4.16 | Charger Output Fuse | Required
4.17 | AC Input Voltmeter | Required
4.18 | AC Input Ammeter | Required
4.19 | Charger DC Voltmeter | Required
4.20 | Charger DC Ammeter | Required
4.21 | Charger DC LC Filter | Required
4.22 | Load Current Ammeter | Required
4.23 | Charger Selector Switch | Required
4.24 | Battery Low DC Alarm (Indicator & Dry Contact) | Required
4.25 | Load Low DC Alarm (Indicator & Dry Contact) | Required
4.26 | Load Hi DC Alarm (Indicator & Dry Contact) | Required
4.27 | Batteries Disconnected (Indicator) | Required
5.Battery Charger Cabinet
5.1 | Type | Flat face
5.2 | Construction | Floor Mounted, Free Standing
5.3 | Ingress protection class | IP42
5.4 | Access for maintenance | Front
5.5 | Body material | Carbon Steel Sheet
5.6 | Thickness of body material | Min.2 mm
5.7 | Finish color | RAL 7032
5.8 | Cable entrance | Bottom and Cable Gland
5.9 | Bottom closing method | By Vendor
5.10 | Cooling method | Natural
5.11 | Space Heater | Required
5.12 | Illumination | Required
5.13 | Noise level | 60dBA
5.14 | Wiring | Power and Control Min.2.5mm², Metering Min.1.5mm²
5.15 | Nameplate | English Black in White Background
5.16 | Earthling System | IT
Note1: Data shown are typical; manufacturer shall provide his own data
Note2: The blank items shall be filled by battery manufacture
6.Batteries
6.1 | Manufacturer | By Vendor
6.2 | Manufacturer Model | By Vendor
6.3 | Standard | IEC 60623, IEEE 1115 2014
6.4 | Quantity | 1 Complete set (2×50% Battery Bank)
6.5 | Service | 24 VDC for F&G System
6.6 | Applicable Specification | BK-GNRAL-PEDCO-000-EL-SP-0005
6.7 | Location | Indoor
6.8 | Battery requirements | By Vendor
6.9 | Battery type | Nickel-Cadmium (IEC60623)
6.10 | Battery charging method | Constant Voltage-Dual Rate and Current Limit with Float/Auto/Equalize/Initial Mode charging
6.11 | Back-up time | 24Hr
6.12 | Emergency Mode Voltage for each cell (Activated by Battery Room Fan Failure) | 1.35 V ± 0.01 V
6.13 | Battery float charging voltage | 1.42 V/Cell
6.14 | Battery Equalize charging voltage ( 0-30Hr Timer and Reset Push Button are required) | 1.46/Cell
6.15 | Battery boost charging voltage ( 0-30Hr Timer and Reset Push Button are required) | 1.55~1.65 V/Cell
6.16 | Battery initial charging voltage ( 0-30Hr Timer and Returnable Switch are required) | 1.75 V/Cell
6.17 | Battery nominal voltage | 1.2 V/Cell
6.18 | Final discharge voltage per cell(V) | 1.14 V/Cell
6.19 | Rated capacity of each cell at 20 ⁰C | Min 1150Ah
6.2 | Re-charging time to 90% Rated Capacity | 24 Hours
6.21 | Required battery ampere-hour (C5) | 1400Ah , SBLE Type
6.22 | Total quantity of cells | 40
6.23 | No. of battery banks | 2
6.24 | No. of batteries per each bank | 20
6.25 | Battery cell dimension (W × D × H ) | By Vendor
6.26 | Battery cell weight | By Vendor
6.27 | Batteries shall be performed from SAFT,ALCAD Batteries | Required
6.28 | All type of Batteries and Battery accessories shall be original and approved by Iranian representative | Required
6.29 | Rate of H2 production during charging | Liter/Cell
6.3 | Required air volume of exchange in battery room | m3/Hours
6.31 | Required air volume of electrolyte | By Vendor
6.32 | Composition of electrolyte | By Vendor
6.33 | Required volume of electrolyte | Liter
6.34 | Required Max. charging current | By Vendor
7.Data sheet for Battery
7.1 | Battery Discharging Rate | Medium Rate
7.2 | Container | Plastic
7.3 | Construction | Vented
8.Accessories & Special Tools
8.1 | Thermometer | Required
8.2 | Hydrometer | Required
8.3 | Voltmeter | Required
8.4 | Battery Racks | Required (Seismic Factor:0.3g)
8.5 | Flame Arrester | Required
8.6 | Stand Type | By Vendor
Note1:Data shown are typical
Note2:The blank items shall be filled by battery manufacture
9.Load Profile Graph
9.1 | T1 :24 H
9.2 | I1 :912 W
9.3 | T2 : 5 Min
9.4 | I2 : 1638 W
10.Data Sheet for Distribution Board
10.1 | Standard | IEC,IPS-M-EL-174(2), IPS-E-EL-100(1)
10.2 | Quantity | 1 Complete set
10.3 | Service | DC Distribution Panel
11.Mechanical specification
11.1 | Mounting type | Floor Mounted, Free Standing
11.2 | Body martial | Carbon Steel Sheet
11.3 | Thickness | Min.2 mm
11.4 | Access for maintenance | Front
11.5 | Protection class | IP42
11.6 | Illumination | Required
11.7 | Space heater | Required
11.8 | Weight | By Vendor
11.9 | Dimensions | By Vendor
11.10 | Name plate | English Black in White Background
11.12 | Finished color | RAL 7032
12.Electrical Specification
12.1 | Rated incoming voltage | 24 VDC
12.2 | Rated insulation voltage | By Vendor
12.3 | Wiring | Power and Control Min.2.5mm²,Metering Min.1.5mm²,
13.Incoming
13.1 | Incoming Cables Size & Tag no. | BK-GCS-PEDCO-120-EL-SL-0006
13.2 | Entry Side | Bottom by Cable Gland
13.3 | Cable Entry | Via Removable Gland Plate
13.4 | Incoming Circuit breaker | MCCB
14.3 | Terminal Type and quantity | By Vendor
13.5 | Circuit breaker construction | Fix
14.Outgoing
14.1 | Outgoing cable size and tag no. | BK-GCS-PEDCO-120-EL-SL-0006
14.2 | Entry side | Bottom by Cable Gland
15.Data Sheet for Distribution Board
15.1 | Cable entry | Via Removable Gland Plate
15.2 | Outgoing circuit breaker | MCCB
15.3 | Circuit breaker constructor | Fix
16.Indicating lights , Alarms and Accessories
16.1 | Battery Low DC alarm | Required ,With Dry Contacts
16.2 | Load Low DC alarm | Required ,With Dry Contacts
16.3 | Load Hi DC alarm | Required ,With Dry Contacts
16.4 | Batteries disconnected | Required
16.5 | Battery voltmeter | Required
16.6 | Battery ammeter | Required
16.7 | Load voltmeter | Required
16.8 | Load ammeter | Required
16.9 | Cable gland | Required
16.10 | Removable gland plate | Required
17.Tests ( Factory Acceptance test and Site Acceptance Test shall be performed By the Vendor )
17.1 | Visual Inspection & Dimensional Check | Required
17.2 | Performance and Function Test | Required
17.3 | Sequence , Operation and Logic Test | Required
17.4 | Dielectric Strength Test | Required
17.5 | Output Voltage and Ripple Check | Required
17.6 | Charger Voltage Adjustment Test | Required
17.7 | THDi% Check | Required
17.8 | Output Regulation / Adjustments Test | Required
17.9 | Alarms Check | Required
17.10 | Autonomy Test | Required
17.11 | Current Limit Test | Required
17.12 | Short Circuit test | Required
17.13 | Other Tests shall be performed in Accordance with IEC60146 (Battery Charger Testing) | Required
17.14 | Hardware and Software for Communication, Programming or Setting up the CPU or MPU Boards (If Required), | Required
18.Accessories And Special Tools
18.1 | MIMIC Panel With LED To Show Operation Condition (shall be finalized by vendor) . | Required
18.2 | Commissioning and two years spare parts shall be provided | Required
18.3 | The Accuracy of all meters shall be better than 1.5% | Required
18.4 | On load break switch-fuse For Battery Banks:Exd type IIC-T3 | Required
18.5 | Training | The Supplier /Vendor shall be assumed the maintenance and repair training course at least for 5 People
18.6 | Battery Room Fan failure (Activated by external Signal ) | Required
19.Electromagnetic Compatibility (EMC)
NOTE: 1. All DC-UPS units shall comply with the requirements for EMC as defined in IEC 62040-2, in order to ensure:Conducted emissions in both, the power supply input and output of the DC- UPS are controlled within acceptable limits;Any electromagnetic disturbance generated by the UPS and its individual components do not exceed a level which would affect the correct operation of both, radio and telecommunications equipment;The DC-UPS has an adequate level of intrinsic immunity to external electromagnetic- and conducted disturbance to enable it to operate as intended. 2. A serial link communication protocol shall be considered for sending alarms and indications to DCS by vendor.
تسهیلات
DATA SHEETS FOR DC CHARGER
NISOC
شماره پیمان:
9184 – 073 - 053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
EL
DT
0002
D04
بسته کاری
GCS
پروژه
BK
D04
D04
D04