## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0002 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2667 |  |  | Transmital Date: 4/21/2024
Document Title: Calculation Note For Indoor Area Lighting System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-2667 |  |  | Transmital Date: 4/21/2024
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-CN-0002_D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised after finalizing or minor comments on architectural detail drawing for control, existing switchgear buildings/Shelters and hazardous area classification layout documents. |  | BK-SUR-ENG-ELE-01-04184 | 2022-05-09 | نقشه معماری تمامی ساختمانها به روز گردید و نقشه های جدید مبنای محاسبات می باشد. |  |  | See below item 6.
2 | According to our telephone conversation following items shall be added or modified: |  | BK-SUR-ENG-ELE-01-04184 | 2022-05-09
2-1 | A separate table shall be added to this document and shall be compared calculated Lux with IPS-E-EL-100 standard to check the result of calculation. |  | BK-SUR-ENG-ELE-01-04184 | 2022-05-09 | اعمال گردید. |  |  | Noted and Closed.
2-2 | The calculation shall be rechecked and modified from point of view the dimensions of the rooms/Shelters and value of standard lux for example for control room. |  | BK-SUR-ENG-ELE-01-04184 | 2022-05-09 | اعمال گردید. |  |  | See below item 7.
2-3 | Lighting calculation for transformer shelter shall be added. |  | BK-SUR-ENG-ELE-01-04184 | 2022-05-09 | محاسبات اتاق ترانس در نظر گرفته شد. |  |  | See below item 8.
3 | Type of lighting fixtures shall be selected base on hazardous area classification. (Gas compressor shelter and chemical injection packages & storage shelter) |  | BK-SUR-ENG-ELE-01-04184 | 2022-05-09 | چراغ های شلتر ها در محدوده ناحیه فرآیندی Explosion Proof در نظر گرفته شده است. |  |  | Noted and Closed.
4 | Workplane/Value Chart shall be added to output reports for each room to check Emin/Emax. For example for corridor its about 0.1 that shall be modified in order to achieve uniform lighting. |  | BK-SUR-ENG-ELE-01-04184 | 2022-05-09 | اعمال گردید. |  |  | Noted and Closed.
5 | Complementary comments will be submitted after received revised documents. |  | BK-SUR-ENG-ELE-01-04184 | 2022-05-09 | در صورت وجود هر گونه کامنت، متعاقبا اعمال خواهد شد. |  |  | Noted and Closed.
6 | See above item 1: In case of any changes in prerequisite documents such as architectural detail drawing, this document shall be revised. |  | BK-SUR-ENG-ELE-01-06400 | 2022-12-14 | اعمال خواهد شد. |  |  | Noted and Closed.
7 | See above item 2-2: According to our telephone conversation, calculated lux shall be rechecked and modified base on IPS-E-EL-100, such as control (In control/CCTV buildings) and office room. Meanwhile the dimension of some rooms such as CO2 room shall be rechecked and modified. |  | BK-SUR-ENG-ELE-01-06400 | 2022-12-14 | تغییرات روشنایی بر اساس کامنتهای کارفرمای محترم در اتاق های کنترل، اتاق کمکی و باتری و بانک خازنی، اتاق CO2 و شلتر یوتیلیتی افزایش یافت. |  |  | Noted and Closed.
8 | See above item 2-3: Transformer shall be shwon in calculation and the transformer room shall be modified base on latest revison of architectural detail drawing. |  | BK-SUR-ENG-ELE-01-06400 | 2022-12-14 | اتاق ترانسفورماتور بر اساس آخرین معماری ساختمان در نظر گرفته شده است. |  |  | Noted and Closed.
9 | It shall be rechecked, 35W LED type lighting fixturers has been used in lighting calculation base on which reference document. (Refer to electrical design criteira and specification for lighting and small power system) |  | BK-SUR-ENG-ELE-01-06400 | 2022-12-14 | مطابق با چراغهای موجود در اطراف اتاق ترانس ایستگاه، چراغهای 20 وات در نظر گرفته شده است. |  |  | Noted and Closed.
10 | According to NISOC comment, the high bay lighting fixturers shall be installed above crain such as fire water pump house shelter. |  | BK-SUR-ENG-ELE-01-06400 | 2022-12-14 | همانطور که در نوت شماره 7 از مدرک جانمایی مشخص است، چراغهای لگنی می بایست بالای جرثقیل سقفی نصب گردد. |  |  | Noted and Closed.
11 | No Comment. Note 1: If any changes in prerequisite documents such as architectural drawing for control, existing switchgear buildings/Shelters or after receiving NISOC comments that affects on document, this document shall be updated and submitted again. Note 2: Mounting type of lighting fixturers (60x60 or Not) shall be rechecked and finalized base on architectural detail drawing for control building. Note 3: Type of lighting fixturers (Ex or not) for shelters will be checked in related lighting layout documents. Note 4: U0 and Emin/Emax for fire water pump house shall be rechecked and modified. |  | BK-SUR-ENG-ELE-01-06832 | 2023-01-30 | در صورت هرگونه تغییر در مدرک معماری, این مدرک بروزرسانی خواهد شد. ارتفاع نصب چراغهای داخل اتاق کنترل بر اساس آخرین نقشه معماری این ساختمان, بروزرسانی گردید. با توجه به اینکه در کاتالوگ چراغهای متال هالید، چراغ ضدانفجار وجود ندارد، در نقشه جانمایی نوع چراغها متناسب با ناحیه خطر مشخص خواهد شد. در ویرایش قبل یک ردیف چراغ بیشتر در زیر شلتر اضافه گردیده است. که میانگین لوکس را از عدد 180 به عدد 238 افزاش یافته است. |  |  | Noted and Closed.
12 | No Comment. Note 1: If any changes in prerequisite documents such as architectural drawing for control, existing switchgear buildings/Shelters or after receiving NISOC comments that affects on document, this document shall be updated and submitted again. |  | BK-SUR-ENG-ELE-02-07755 | 2023-05-30 | در صورت وجود هر گونه کامنت، مدرک مورد ویرایش قرار خواهد گرفت. |  |  | Noted and Closed.
13 | No Comment. |  | BK-SUR-ENG-ELE-03-09240 | 2024-04-27 | سپاسگزارم
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: