## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
HAZARD SOURCE LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 5
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | SA | LI | 0001 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
HAZARD SOURCE LIST نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | OCT.2024 |  | IFA |  |  |  | R.Yazdani |  |  | M.Fakharian |  | M.Sadeghian
D02 |  | NOV.2023 |  | IFA |  |  |  | A.Saber |  |  | M.Fakharian |  | S.Faramarzpour
D01 |  | AUG.2022 |  | IFA |  |  |  | A.Saber |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | FEB.2022 |  | IFC |  |  |  | A.Saber |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number:F0Z-709002
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
HAZARD SOURCE LIST
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 5
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | SA | LI | 0001 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | X |  | X |  |  |  | 67
4 | X | X | X |  | X |  |  |  | 68
5 | X |  | X | [5 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## 3
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
HAZARD SOURCE LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 3 از 5
053-073-9184 |  |  | BK |  | GCS |  | PEDCO |  | 120 |  | SA |  | LI |  | 0001 |  | D03
ITEM No. | TAG NUMBER | DESCRIPTION | FLUID | TYPE OF RELEASE | [8 empty] | IGNITION POINT('C) | VAPOR DENSITY (L/H) (4) | MAX OPERATING CONDITION |  | DANGEROUS ITEM | CLASSIFICATION |  | TEMP | UFL | LFL | REMARK
|  |  |  | Grades of release (1) |  |  | Location (2) |  |  | Vent (3) |  |  |  |  | TEMP.('C) | PRESS.(BARG) |  | GAS GROUP | ZONE |  | VOL.%
|  |  |  | C | P | S | O | E | S | N | I | F
1 | V-2101A/B/C | 1ST Stage Gas Comression Suction Drum | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | L | 36 | 4.9 | HYDROCARBON GAS | IIA | 2 | T3 |  |  | FIG 48
2 | V-2102A/B/C | 2 Nd Stage Gas Comression Suction Drum | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | L | 60 | 18.1 | HYDROCARBON GAS | IIA | 2 | T3 |  |  | FIG 48
3 | V-2103 | 2 Nd Stage Gas Comression Discharge Drum | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | L | 60 | 53.9 | HYDROCARBON GAS | IIA | 2 | T3 |  |  | FIG 48
4 | V-2104 | Slug Catcher Drum | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | L | 15~40 | 5.3 | HYDROCARBON LIQ+GAS | IIA | 2 | T3 |  |  | FIG 48
5 | V-2105 | Inlet Knock Out Drum | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | L | 15~40 | 5.1 | HYDROCARBON GAS | IIA | 2 | T3 |  |  | FIG 48
6 | V-2107 | Glycol Sump Drum | TEG+HC | [9 empty] | > 200 | H | AMB | 0.1 | TEG+HYDROCARBON | IIA | 1 & 2 | T3 |  |  | FIG 48 | bar: Grades of release (1) S; Location (2) S to Vent (3) N
7 | V-2201 | Flare K.O. Drum | HC + H2S | [9 empty] | > 200 | H/L | AMB | 0.2~0.5 | HYDROCARBON GAS | IIA | 1 & 2 | T3 |  |  | FIG 48 | bar: Grades of release (1) S; Location (2) S to Vent (3) N
8 | V-2202 | Close drain drum | HC + H2S | [9 empty] | > 200 | H | AMB | 0.2~0.5 | HYDROCARBON LIQ+ GAS | IIA | 1 & 2 | T3 |  |  | FIG 48 | bar: Grades of release (1) S; Location (2) S to Vent (3) N
9 | V-2205 | Fuel Gas K.O. Drum | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | L | 15~40 | 4.9 | HYDROCARBON GAS | IIA | 2 | T3 |  |  | FIG 48
10 | V-2206 | Diesel Oil Drum | DIESEL OIL | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | H | AMB | ATM. | HYDROCARBON GAS | IIA | 2 | T3 |  |  | FIG 8
11 | TK-2102 | Lean Glycol Storage Tank | TEG | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | H | AMB | 0.1 | TEG | IIA | 2 | T3 |  |  | FIG 6
12 | C-2101 A/B/C | 1 St Stage Gas Compressor | HC + H2S | Grades of release (1) S: S; Location (2) O: O*; Vent (3) N: N | > 200 | L | 150 | 18.1 | HYDROCARBON GAS | IIA | 2 | T3 |  |  | FIG 52
13 | C-2102 A/B/C | 2Nd Stage Gas Compressor | HC + H2S | Grades of release (1) S: S; Location (2) O: O*; Vent (3) N: N | > 200 | L | 150 | 53.5 | HYDROCARBON GAS | IIA | 2 | T3 |  |  | FIG 52
14 | AE-2101 A/B/C | 1 St Stage Gas Compressor Air Cooler | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | L | 150 | 18.1 | HYDROCARBON GAS | IIA | 2 | T3 |  |  | FIG 48
15 | AE-2102 A/B/C | 2 Nd Stage Gas Compressor Air Cooler | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | L | 150 | 53.5 | HYDROCARBON GAS | IIA | 2 | T3 |  |  | FIG 48
18 | P-2101 A/B | Slug Pumps | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | LIGHTER | AMB | 31 | liquid HYDROCARBON | IIB | 2 | T3 |  |  | FIG 51
19 | P-2102 | Glycol Manual Pump | TEG | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | - | AMB | 3 | GLYCOL | IIA | 2 | T4 |  |  | FIG 51
20 | P-2103 A/B | Glycol Transfer Pumps | TEG | Grades of release (1) S: S; Location (2) O: O; Location (2) S: S; Vent (3) N: N | > 200 | - | AMB | 2 | SLUG | IIA | 2 | T4 |  |  | FIG 51
21 | P-2104 | Glycol Drain Pumps | TEG+HC | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | HEAVIER | AMB | 2 | HYDROCARBON GAS | IIA | 1 & 2 | T4 |  |  | FIG 51
22 | P-2201A/B | LP Flare K.O. Drum Pumps | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | LIGHTER | AMB | 2.5 | HYDROCARBON GAS | IIB | 1 & 2 | T3 |  |  | FIG 51
23 | P-2202A/B | Closed Drain Pumps | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N; Vent (3) I: IFA | > 200 | LIGHTER | AMB | 2.5 | HYDROCARBON LIQ | IIB | 1 & 2 | T3 |  |  | FIG 51
24 | P-2203A/B | Sump Pumps | OILY WATER | Grades of release (1) S: S; Location (2) O: O; Location (2) S: S; Vent (3) N: N | > 200 | - | AMB | 2 | HYDROCARBON OIL | IIB | 1 & 2 | T3 |  |  | FIG 51
25 | P-2206 | Diesel oil Pump | DIESEL | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | - | AMB | 2 | DIESEL | N.A | 2 | T3 |  |  | FIG 51
26 | PK‐2101 | Dehydration Package | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Location (2) S: S; Vent (3) N: N | > 200 | LIGHTER | 60 | 53.5 | HYDROCARBON +TEG+WATER | IIB | 2 | T4 |  |  | FIG 48
27 | PK‐2206 | Diesel Generator Package | DIESEL | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N |  | - | AMB | ATM. | DIESEL | N.A | 2 | T3 |  |  | FIG 55
28 | PK-2207 | Corrosion Inhibitor Package | DIESEL | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N |  | - | AMB | ATM. | COROSION INHIBITO | N.A | 2 | T3 |  |  | FIG 55
29 | PK-2208 | Methanol Injection Package | METHANOL | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N |  | LIGHTER | AMB | 0.1 |  | IIA | 2 | T2 |  |  | FIG 55
30 | FST-2201 | LP Flare Stack | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N |  | LIGHTER | AMB | 0.5 | HYDROCARBON GAS | IIA | 2 | T3 |  |  | FIG 14
31 | IG-2201 | LP Flare Ignation Package | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N |  | LIGHTER | AMB | 4.9 | HYDROCARBON GAS | IIA | 2 | T3 |  |  | FIG 55
32 | SU-2201 | LP Flare K.O Drum and Close Drain Sump | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Location (2) S: S; Vent (3) N: N |  | LIGHTER | AMB | ATM. | HYDROCARBON GAS | IIA | 1 | T3 |  |  | clause 10.12
33 | SU-2202 | Oily Water Sump | HC | Grades of release (1) S: S; Location (2) O: O; Location (2) S: S; Vent (3) N: N |  | LIGHTER | AMB | ATM. | HYDROCARBON GAS | IIB | 1 | T3 |  |  | clause 10.12
34 | PR-1002 | Golkhari Pig Reciever | HC | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N |  | LIGHTER | AMB | ATM. | HYDROCARBON GAS | IIB | 2 | T3 |  |  | FIG 49
35 | PL-3201 | Pig Launcher | HC | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N |  | LIGHTER | AMB | ATM. | HYDROCARBON GAS | IIB | 2 | T3 |  |  | FIG 49
35 | General | ANY PIPING FITTING & CONNECTION ( INCLIUDE FLANGES/ VALVES/ AND ANY SCREWED CONNECTIONS) | HC | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N |  | LIGHTER | AMB | ATM. |  | IIB | 2 | T3 |  |  | see section 10.15 API 505
NOTE1: Class III liquids normally do not produce vapors of sufficient quantity to be considered for electrical classification purposes. Class III liquids will release vapor in the flammable range at their surfaces if heated above their flash points, but the extent of the classified location ordinarily will be very small and near the point of release. NOTE2: Liquid which will be drained to burn pit during maintenance activities should be burned to prevent environmental pollution, but if it emptied by any pumps, they should be certified for above specified area classification.
DEFINITION:
(1) Grades of release: | [12 empty] | (2) | Location:
"C":Continuous or is expected to occur for long periods. | [13 empty] | "O": open area;"O*": Open area under shelter; "E":Enclosed; "S": Sumped;
"P": Primary; A release that can be expected to occur periodically or occasionally during normal operation | [12 empty] | (3) | Vent:
"S":secondary: A release that is not expected to occur is likely to do so only in infrequently and for short periods. | [13 empty] | "N": Natural; "I":Inadequate; "F": Forced;
[13 empty] | (4) | Vapor Density:
[14 empty] | 'L'': Lighter than Air |  |  | 'H'': Hevier than Air
D03
D02

## 4
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
HAZARD SOURCE LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه | شماره صفحه:4 از 5
053-073-9184 |  |  | BK |  | GCS |  | PEDCO |  | 120 |  | SA |  | LI |  | 0001 |  | D03
ITEM No. | TAG NUMBER | DESCRIPTION | FLUID | TYPE OF RELEASE | [8 empty] | IGNITION POINT('C) | VAPOR DENSITY (L/H) (4) | MAX OPERATING CONDITION |  | DANGEROUS ITEM | CLASSIFICATION |  | TEMP | UFL | LFL | REMARK
|  |  |  | Grades of release (1) |  |  | Location (2) |  |  | Vent (3) |  |  |  |  | TEMP.('C) | PRESS.(BARG) |  | GAS GROUP | ZONE |  | VOL.%
|  |  |  | C | P | S | O | E | S | N | I | F
1 | V-2101A/B/C | 1ST Stage Gas Comression Suction Drum | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | LIGHTER | 36 | 4.9 | HYDROCARBON GAS | IIB | 2 | T3 |  |  | FIG 48
2 | V-2102A/B/C | 2 Nd Stage Gas Comression Suction Drum | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | LIGHTER | 60 | 18.1 | HYDROCARBON GAS | IIB | 2 | T3 |  |  | FIG 48
3 | V-2103 | 2 Nd Stage Gas Comression Discharge Drum | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | LIGHTER | 60 | 53.9 | HYDROCARBON GAS | IIB | 2 | T3 |  |  | FIG 48
4 | V-2104 | Slug Catcher Drum | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Location (2) S: S; Vent (3) N: N | > 200 | LIGHTER | 15~40 | 5.3 | HYDROCARBON LIQ+GAS | IIB | 2 | T3 |  |  | FIG 48
5 | V-2105 | Inlet Knock Out Drum | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | LIGHTER | 15~40 | 5.1 | HYDROCARBON GAS | IIB | 2 | T3 |  |  | FIG 48
6 | V-2106 | Degassing Vessel | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | LIGHTER | 15~40 | 0.5 | LIQ HYDROCARBON | IIA | 2 | T3 |  |  | FIG 48
7 | V-2107 | Glycol Sump Drum | TEG+HC | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | - | AMB | 0.1 | TEG+HYDROCARBON | IIA | 1 & 2 | T4 |  |  | FIG 48
8 | V-2201 | Flare K.O. Drum | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Location (2) S: S; Vent (3) N: N | > 200 | LIGHTER | AMB | 0.2~0.5 | HYDROCARBON GAS | IIB | 1 & 2 | T3 |  |  | FIG 48
9 | V-2202 | Close drain drum | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | LIGHTER | AMB | 0.2~0.5 | HYDROCARBON LIQ+ GAS | IIB | 2 | T3 |  |  | FIG 48
10 | V-2205 | Fuel Gas K.O. Drum | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | LIGHTER | 15~40 | 4.9 | HYDROCARBON GAS | IIB | 2 | T3 |  |  | FIG 48
11 | V-2206 | Diesel Oil Drum | DIESEL OIL | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | - | AMB | ATM. | HYDROCARBON GAS | N.A | 2 | T3 |  |  | FIG 8
12 | TK-2101 | Slug Storage Tank | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Location (2) S: S; Vent (3) N: N | > 200 | LIGHTER | 15~40 | 0.5 | liquid HYDROCARBON | IIA | 2 | T3 |  |  | FIG 6
13 | TK-2102 | Lean Glycol Storage Tank | TEG | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | - | AMB | 0.1 | HYDROCARBON GAS | IIA | 2 | T4 |  |  | FIG 6
14 | C-2101 A/B/C | 1 St Stage Gas Compressor | HC + H2S | Grades of release (1) S: S; Location (2) O: E; Vent (3) N: N |  | LIGHTER | 150 | 18.1 | HYDROCARBON GAS | IIB | 2 | T3 |  |  | FIG 52
15 | C-2102 A/B/C | 2Nd Stage Gas Compressor | HC + H2S | Grades of release (1) S: S; Location (2) O: E; Vent (3) N: N |  | LIGHTER | 150 | 53.5 | HYDROCARBON GAS | IIB | 2 | T3 |  |  | FIG 52
16 | AE-2101 A/B/C | 1 St Stage Gas Compressor Air Cooler | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N |  | LIGHTER | 150 | 18.1 | HYDROCARBON GAS | IIB | 2 | T3 |  |  | FIG 48
17 | AE-2101 A/B/C | 2 Nd Stage Gas Compressor Air Cooler | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N |  | LIGHTER | 150 | 53.5 | HYDROCARBON GAS | IIB | 2 | T3 |  |  | FIG 48
16 | P-2101 A/B | Slug Pumps | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | H | AMB | 31 | Liquid HYDROCARBON | IIA | 2 | T3 |  |  | FIG 51
17 | P-2102 | Glycol Manual Pump | TEG | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | H | AMB | 3 | GLYCOL | IIA | - | T3 |  |  | FIG 51
18 | P-2103 A/B | Glycol Transfer Pumps | TEG | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | H | AMB | 2 | GLYCOL | IIA | - | T3 |  |  | FIG 51
19 | P-2104 | Glycol Drain Pumps | TEG+HC | [9 empty] | > 200 | H | AMB | 2 | HYDROCARBON GAS | IIA | 1 & 2 | T3 |  |  | FIG 51 | bar: Grades of release (1) S; Location (2) S to Vent (3) N
20 | P-2201A/B | LP Flare K.O. Drum Pumps | HC + H2S | [9 empty] | > 200 | H | AMB | 2.5 | HYDROCARBON GAS | IIA | 1 & 2 | T3 |  |  | FIG 51 | bar: Grades of release (1) S; Location (2) S to Vent (3) N
21 | P-2202A/B | Closed Drain Pumps | HC + H2S | [9 empty] | > 200 | H | AMB | 2.5 | HYDROCARBON LIQ | IIA | 1 & 2 | T3 |  |  | FIG 51 | bar: Grades of release (1) S; Location (2) S to Vent (3) N
22 | P-2203A/B | Sump Pumps | OILY WATER | [9 empty] | > 200 | H | AMB | 2 | HYDROCARBON OIL | IIA | 1 & 2 | T3 |  |  | FIG 51 | bar: Grades of release (1) S; Location (2) S to Vent (3) N
23 | P-2206 | Diesel oil Pump | DIESEL | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | H | AMB | 2 | DIESEL | IIA | - | T3 |  |  | FIG 51
24 | PK‐2101 | Dehydration Package | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | L | 60 | 53.5 | HYDROCARBON +TEG+WATER | IIA | 2 | T3 |  |  | FIG 48
25 | PK‐2206 A/B | Diesel Generator Package | DIESEL | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | H | AMB | ATM. | DIESEL | N.A | 2 | T3 |  |  | FIG 55
26 | PK-2207 | Corrosion Inhibitor Package | DIESEL | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | H | AMB | ATM. | COROSION INHIBITOR | IIA | 2 | T3 |  |  | FIG 55
27 | FST-2201 | LP Flare Stack | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | L | AMB | 0.5 | HYDROCARBON GAS | N.A | N.A | N.A |  |  | FIG 14
28 | IG-2201 | LP Flare Ignation Package | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | L | AMB | 4.9 | HYDROCARBON GAS | IIA | 2 | T3 |  |  | FIG 55
29 | SU-2201 | LP Flare K.O Drum and Close Drain Sump | HC + H2S | Grades of release (1) S: S; Location (2) O: O; Location (2) S: S; Vent (3) N: N | > 200 | L | AMB | ATM. | HYDROCARBON GAS | IIA | 1 & 2 | T3 |  |  | Figure 57 clause 10.12
30 | SU-2202 | Oily Water Sump | HC | Grades of release (1) S: S; Location (2) O: O; Location (2) S: S; Vent (3) N: N | > 200 | L | AMB | ATM. | HYDROCARBON GAS | IIA | 1 & 2 | T3 |  |  | Figure 57 clause 10.12
31 | PR-2002 | Golkhari Pig Reciever | HC | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | L | AMB | ATM. | HYDROCARBON GAS | IIA | 2 | T3 |  |  | FIG 49
32 | PL-3201 | Pig Launcher | HC | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | L | AMB | ATM. | HYDROCARBON GAS | IIA | 2 | T3 |  |  | FIG 49
33 | General | Battery Room | H2 | Grades of release (1) S: S; Location (2) E: E; Vent (3) F: F | 500 | L | 25 | ATM. | HYDROGEN GAS | IIC | 1 & 2 | T3 |  |  | see section 11.23 API 505
34 | General | ANY PIPING FITTING & CONNECTION ( INCLIUDE FLANGES/ VALVES/ AND ANY SCREWED CONNECTIONS) | HC | Grades of release (1) S: S; Location (2) O: O; Vent (3) N: N | > 200 | L | AMB | ATM. | HYDROCARBON | IIA | 2 | T3 |  |  | see section 10.15 API 505
NOTE1: Class III liquids normally do not produce vapors of sufficient quantity to be considered for electrical classification purposes. Class III liquids will release vapor in the flammable range at their surfaces if heated above their flash points, but the extent of the classified location ordinarily will be very small and near the point of release. NOTE2: Liquid which will be drained to burn pit during maintenance activities should be burned to prevent environmental pollution, but if it emptied by any pumps, they should be certified for above specified area classification.
DEFINITION:
(1) Grades of release: | [12 empty] | (2) | Location:
"C":Continuous or is expected to occur for long periods. | [13 empty] | "O": open area;"O*": Open area under shelter; "E":Enclosed; "S": Sumped;
"P": Primary; A release that can be expected to occur periodically or occasionally during normal operation | [12 empty] | (3) | Vent:
"S":secondary: A release that is not expected to occur is likely to do so only in infrequently and for short periods. | [13 empty] | "N": Natural; "I":Inadequate; "F": Forced;
[13 empty] | (4) | Vapor Density:
[14 empty] | 'L'': Lighter than Air |  |  | 'H'': Hevier than Air
D03

## 5
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
HAZARD SOURCE LIST
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 5
053-073-9184 |  | BK | GCS | PEDCO | 120 | SA | LI | 0001 | D03
IEC
Component |  |  | Mol % Winter | Mol % Summer | Ignition point © | Boiling point © | Flash point © | Gas Group | Temp. Class | LFL VOL% | UFL VOL%
H2S |  |  | 1.8675 | 2.8046 | 260 | -59.652 | -82.4 | IIB | T3 | 4 | 44
Nitrogen |  |  | 0.1013 | 0.1279 | NF | -195.8 | N/A | N/A | N/A | N/A | N/A
CO2 |  |  | 1.6716 | 3.454 | NF | -78.552 | N/A | N/A | N/A | N/A | N/A
Methane |  |  | 78.3733 | 57.4395 | 600 | -161.525 | -188 | IIA | T1 | 5 | 15
Ethane |  |  | 11.8553 | 17.3785 | 515 | -88.6 | -135 | IIA | T1 | 3 | 12.5
Propane |  |  | 4.219 | 10.5491 | 450 | -42.102 | -104 | IIA | T2 | 2.1 | 9.5
i-Butane |  |  | 0.3278 | 1.2694 | 460 | -11.73 | -83 | IIA | T1 | 1.8 | 8.4
n-Butane |  |  | 0.7078 | 2.9325 | 288 | -0.50199 | -60 | IIA | T3 | 1.9 | 8.5
i-Pentane |  |  | 0.1292 | 0.7577 | 420 | 27.878 | -49 | IIA | T2 | 1.32 | 9.16
n-Pentane |  |  | 0.0786 | 0.492 | 243 | 36.059 | -40 | IIA | T3 | 1.5 | 7.8
n-Hexane |  |  | 0.0941 | 0.8069 | 225 | 68.73 | -26 | IIA | T3 | 1.1 | 7.5
n-Heptane |  |  | 0.0243 | 0.2854 | 204 | 98.42 | -4 | IIA | T3 | 1 | 6.7
n-Octane |  |  | 0.0053 | 0.0787 | 206 | 125 | 13 | IIA | T3 | 1 | 6.5
n-Nonane |  |  | 0.0016 | 0.0295 | 205 | 151 | 31 | IIA | T3 | 0.8 | 2.9
n-Decane |  |  | 0 | 0.0098 | 210 | 174.1 | 46 | IIA | T3 | 0.7 | 5.4
N-C11 |  |  | 0 | 0 | NA | 193 ~ 197 | 62 | IIA | T3 | N/A | N/A
C12+ |  |  | 0 | 0 | NA | NA | NA | N/A | N/A | N/A | N/A
Water (H2O) |  |  | 0.5433 | 1.5844 | NF | 100 | N/A | N/A | N/A | N/A | N/A
FLUID | [7 empty] | IIA | T3
NOTE:
1.This hazardous area schedule is prepared in accordance with API 505 & NFPA 497.
2.Electrical Apparatus subgroup and temperature class have been classified according to IEC 79, see Institute of Petroleum (IP) Model
3.All adequately vented enclosed areas are Zone 2 to the extent of the enclosed area
4.All floor drain sumps in the Hazardous area are considered to be Zone 1 below grade , with 0.5 metre radius Zone 2 above grade .
5. Due to the nature of the hydrocarbon gases and liquids processed all vents and drains in hydrocarbon service are hard piped to the appropriate
flare or drain system header Consequently these connections are deemed non-hazardous.
6. Liquids of Classes II (1) or III (1) or unclassified are normally non-hazardous on release with a small Zone 1 around roof vents and openings.
7. As there are so many devices with different composition, for exact deatil to be referred to Process Simulation Report ; BK-GCS-PEDCO-120-PR-RT-0003
NA | Not Available | NF | Not Flammable |  | N/A | Not Applicable