## Sheet1
Requisition Reference Title : نگهداشت و افزایشتولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوري بینک
vendor Name: Sangan sanat |  | Deviation List |  |  | Date: 19-May-2024
|  | Requisition Reference No.: BK-GCS-PEDCO-120-IN-MR-0010_D01 |  |  | Rev:01
No. | Document No. & Clause No. | Project Requirement | Vendor replay | Vendor replay2 | Acceptance / Rejection by PURCHASER
1 | Datasheet of differential pressure gauge ITEM 25 | Accuracy is ±0.5% of F.S. | 2-Accuracy for differential pressure gauge is 1.6% F.S.D (In operational conditions, accuracy cannot be better than this. Otherwise, it is Better to use DP transmitter. Please refer to Deviation list
2 | Datasheet of pressure gauge TAGs: PG-2221 PG-2251 PG-2274 PG-2282 PG-2283 PG-2295 | element type is Diaphragm | for pressure range higher than 0.6 bar , bordun tube is used | please be informed pressure range of these tags are 1 bar & 2.5 bar. Capusule & diaphragm cannot measure this range. Only burdoun can be used.
3 | Datasheet of pressure gauge TAGs: PG-2162 PG-2161 PG-2298 PG-2292 PG-2294 | Case is Liquid. Filled | for pressure gauge lower than 0.6 bar (diaphragm type) , Case cannot be filled. | Please be Informed , due to the low pressure of these gauges, the oil disrupts the performance of the calibration and the accuracy of the gauge decreases. As a manufacturer, it is not recommended to use oil and it is not possible.
4 | 4- GCS_TCL for PG-D00 - Sangan Sanat item 28 | Diaphragm gauges shall also be solid front acc. to project data sheet | Diaphragm & capsule pressure gauge is not solid front (safety is S2) Note: Solid Front gauge is used to protect against high pressures.
5 | 4- GCS_TCL for PG-D00 - Sangan Sanat item 34 | Regarding differential pressure gauge, these devices shall also be safety pattern type. | Differential pressure gauge diaphragm type is not solid front (safety is S2) Note: Solid Front gauge is used to protect against high pressures. | Is not applicable.
6 | TCL -rev01 item 30 | About mentioned deviation regarding case filling of diaphragm pressure gauges, please be noted that as per EN-837-3 section 9.8, diaphragm gauges can also be liquid filled. So, project requirements shall be followed. | Is not applicable. due to the low pressure of these gauges, the oil disrupts the performance of the calibration and the accuracy of the gauge decreases. As a manufacturer, it is not recommended to use oil and it is not possible.
7
7