## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-SA-PI-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2590 |  |  | Transmital Date: 2/20/2024
Document Title: P&ID - Fire Water Network |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-SA-TR-2590 |  |  | Transmital Date: 2/20/2024
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-SA-PI-0001_D05 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
| لازم است PRESSURE SENSING LINE مربوئط به پمپ P-2301 A بر اساس استاندارد NFPA 20 اصلاح شود. |  | 1402-2294-8682 | 1403/01/15 | اصلاح گردید.
1 | لازم است تا مدرک FIRE WATER NETWORK مطابق با استاندارد NFPA 20 مورد بازبینی و اصلاح قرار گیرد. به عنوان نمونه اصلاح مسیر PRESSURE-SENSING LINE تلمبه P-2301 A صفحه 2/8(قرار دادن شیرهای یک طرفه) |  | 1403-2291-48643 | 1403/02/10 | با توجه به استاندارد NFPA 20 ، مدرک اصلاح شد.
2 | در مدرک FIRE WATER NETWORK صفحه 2/8 وضعیت پایپینگ و تجهیزات ابزار دقیق برای تلمبه های P-2302A/B یکسان نمی باشند که باید اصلاح گردد. |  | 1403-2291-48643 | 1403/02/10 | اصلاح گردید.
3
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: