## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MECHANICAL DATA SHEETS FOR ELEVATED POTABLE WATER TANK
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 6
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | ME | DT | 0011 | D04
طرح نگهداشت و افزایش تولید 27 مخزن
MECHANICAL DATA SHEETS FOR ELEVATED POTABLE WATER TANK
نگهداشت و افزایش تولید میدان نفتی بینک
D04 |  | OCT.2024 |  | AFC |  |  |  | V.Amjadi |  |  | M.Fakharian |  | M.Sadeghian
D03 |  | JUN.2024 |  | IFA |  |  |  | V.Amjadi |  |  | M.Fakharian |  | M.Sadeghian
D02 |  | NOV.2022 |  | IFA |  |  |  | H.Adineh |  |  | M.Fakharian |  | M. Mehrshad
D01 |  | DEC.2021 |  | IFC |  |  |  | H.Adineh |  |  | M.Fakharian |  | M. Mehrshad
D00 |  | NOV.2021 |  | IFC |  |  |  | H.Adineh |  |  | M.Fakharian |  | M. Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: |  |  | F0Z-708842
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MECHANICAL DATA SHEETS FOR ELEVATED POTABLE WATER TANK
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 6
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | ME | DT | 0011 |  | D04
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  | X |  | 65
2 | X | X | X |  | X |  | X |  | 66
3 | X | X | X | [5 empty] | 67
4 | X | X | X |  | X |  |  |  | 68
5 | X | X | X |  | X |  |  |  | 69
6 | X | X | X |  | X |  |  |  | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Note 1
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MECHANICAL DATA SHEETS FOR ELEVATED POTABLE WATER TANK
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 6
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | ME | DT | 0011 | D04
General Notes
| 1. | THE ASTERISK * DENOTES INFORMATION AND/OR CONFIRMATION REQUIRED FROM VENDOR. THE VENDOR SHALL BE FULLY RESPONSIBLE
FOR DESIGN AND SUPPLY OF THE TANK. THE TANK SHALL BE SUPPLIED IN ACCORDANCE WITH PROJECT 'SPECIFICATION FOR STORAGE TANK
, DOC. NO. BK-GNRAL-PEDCO-000-ME-SP-0002. THE MANUFACTURER SHALL CALCULATE THICKNESS AND LOADS OF THE TANK.
| 2. | ALL MATERIAL, THICKNESS, CORROSION ALLOWANCE, DIMENSIONS AND THEIR SUITABILITY FOR THE FLUID AT DESIGN CONDITION TO BE CONFIRMED
| MECHANICAL DATA SHEETS FOR ELEVATED POTABLE WATER TANK | BY VENDOR.
| 3. | ALL MATERIAL SHALL BE NEW AND UNUSED.
| 4. | RF: RAISED FACE , SO: SLIP ON, WN: WELD NECK.
| 5. | ACC. TO ANSI B16.5. & B16.47 SERIE A.
| 6. | BOLT HOLES FOR FLANGES SHALL STRADDLE TANK NATURAL CENTRE LINES FOR HORIZONTAL NOZZLES.
| 7. | Deleted.
| 8. | VENDOR SHALL SUPPLY DETAILS OF ALL WELDING CONNECTIONS AND GIVE GENERAL SPECIFICATION OF USED MATERIALS.
| 9. | TANK SHALL BE THOROUGHLY CLEANED OUTSIDE AND INSIDE AND FREE FROM RUST,SLAG,SCALE, WELD SPATTER & FOREIGN MATTER.
| 10. | ALL REINFORCING PADS SHALL HAVE ONE NPT 6mm TELL TALE HOLE.
| 11. | SHALL BE HOT DIP GALVANIZED PER 'IPS-E-TP-100', SYSTEM '8C' OF TABLE '2' (WITH MIN. DFT 140 MIC.).
| 12. | LIQUID LEVELS ARE FROM BELOW OF THE TANK FIRST SHELL COURSE PLATE.
| 13. | INLET NOZZLE SHALL BE COMPLETED WITH INTERNAL LONG RADIUS ELBOW, DIP PIPE AND WEAR PLATE UNDER PIPE.
SYPHON BREKER HOLE IS REQUIRED AT BELOW.
| 14. | ALL INLET AND OUTLET CONNECTIONS TO TANK SHALL BE ISOLATED.
| 15. | SITE CONDITION SUCH AS SEISMIC ZONE, SOIL PROFILE, WIND VELOCITY, WIND EXPOSURE SHALL AS PER PROJECT 'PROCESS BASIS OF DESIGN'
DOCUMENT No. BK-GNRAL-PEDCO-000-PR-DB-0001.
| 16. | ACCESS LADDER & PLATFORM TO BE CONSIDERED.
| 17. | SPECIFIED ACCESSORIES AND ATTACHMENTS SHALL BE SUPPLIED BY VENDOR.
| 18. | FOR INSTRUMENTS INSTALLATION ON THE STAND PIPE, 2", #300 FLANGES SHALL BE CONSIDERED AS PER BK-GNRAL-PEDCO-000-IN-SP-0001 .
| 19. | INSULATION SHALL BE AS PER PROJECT 'SPECIFICATION FOR INSULATION', DOCUMENT NO "BK-GENRAL-PEDCO-000-PI-SP-0019".
| 20. | FIRE PROOFING REQUIREMENT WILL BE SPECIFIED AS PER RESULT OF FIRE PROOFING ZONE LAYOUT.
| 21. | FOR STANDARD DETAIL OF EARTH LUG EXECUTION REFER TOTHE PROJECT "STANDARD DETAIL DRAWING FOR STORAGE
TANKS DOC. NO. "BK-GNRAL-PEDCO-000-ME-DW-0002" AND PROVIDE MINIMUM TWO EARTHING TERMINALS AND TWO CABLES PER TANK.
| 22. | LOCATION OF CONNECTIONS SHALL BE FINALIZED LATTER.
| 23. | MANWAYS SHALL BE SUPPLIED COMPLETE WITH BLIND FLANGE, EXTERNAL GRAB HANDLES, INTERNAL GRAB HANDLE AND LADDER RUNGS, NUTS,
BOLTING, GASKET AND PROOF LOAD TEST DAVITS. DAVITS SHALL BE PROOF LOAD TESTED ON THE VESSELS TO 1.5 X SAFE WORKING LOAD (SWL) AND
SHALL BE MARKED ACCORDINGLY.
| 24. | VENDOR SHALL SUPLLY FOLLOWING ITEMS AS SPARE PARTS: | 24. | VENDOR SHALL SUPLLY FOLLOWING ITEMS AS SPARE PARTS:
|  | TWO YEARS SPARE PARTS & COMMISSIONING SPARE PARTS SHALL BE CONSIDERED AS PER DOCUMMENT NO. E&C-QC-SP-1. |  | TWO YEARS SPARE PARTS & COMMISSIONING SPARE PARTS SHALL BE CONSIDERED AS PER DOCUMMENT NO. E&C-QC-SP-1.
| 25. | ALL DIMENSIONS ARE IN "MM" UNLESS OTHERWISE SPECIFIED. | 25. | ALL DIMENSIONS ARE IN "MM" UNLESS OTHERWISE SPECIFIED.
| 26. | VENDOR SHALL CALCULATED THE MECHANICAL CALCULATION AND SUBMITTED THE CALCULATION BOOK FOR TANK. | 26. | VENDOR SHALL CALCULATED THE MECHANICAL CALCULATION AND SUBMITTED THE CALCULATION BOOK FOR TANK.
| 27. | ELEVATED POTABLE WATER TANK GEOMETRY SHALL BE IN ACCORDANCE WITH IPSSTANDARD DRAWING NO. IPS-D-CE-412.

## TK-2209(1)
NISOC | [8 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MECHANICAL DATA SHEETS FOR ELEVATED POTABLE WATER TANK
شماره پیمان: | [8 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال |  |  | نسخه |  | شماره صفحه: 4 از 6
9184 – 073 - 053 | [8 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | ME |  | DT | 0011 |  |  | D04
Mech. Data Sheets for Elevated Potable Water Tank (TK-2209) / Sheet 4 of 6
Rev. | GENERAL DATA
| 1 | General Information
| 2 | PROJECT |  | : | [14 empty] | COMPANY |  | : |  | NISOC
| 3 | LOCATION |  | : | BINAK, 20 km NORTHWEST of GENAVEH CITY | [13 empty] | ALTITUDE |  | :
| 4 | ITEM NO. |  | : | TK-2209 | [13 empty] | QUANTITY |  | : |  | 1 SET
| 5 | FLUID |  | : | POTABLE WATER | [13 empty] | SERVICE |  | : |  | STORAGE TANK
| 6 | Process Data
| 7 | NOMINAL / WORKING CAPACITY | [9 empty] | 25 / 20 | [5 empty] | (m3) | OPERATING TEMPERATURE | [7 empty] | AMB. |  |  | (ºC)
| 8 | DIMENSION ( INTERNAL DIA./ HEIGHT) | [9 empty] | 3500 x 2600 | [5 empty] | (mm) | OPERATING PRESSURE | [7 empty] | ATM. |  |  | (barg)
| 9 | ELEVATION (L. L.-OUTLET FLANGE C.L.) | [9 empty] | 20000 | [5 empty] | (m)
| 10 | H.L.L. (NOTE 12) | [9 empty] | 2250 | [5 empty] | (mm)
| 11 | DENSITY | [9 empty] | 1000 | [5 empty] | (kg/m³)
| 12 | Design Data
| 13 | INSTALLATION POSITION : | [6 empty] | HORIZONTAL |  |  |  |  | VERTICAL |  | YES |  |  | TANK TYPE: |  | CYLINDERICAL SELF SUPPORTED CONE ROOF
| 14 | SHELL / BOTTOM / ROOF THICKNESS | [8 empty] | * (NOTE 1) | [6 empty] | (mm) | ROOF SLOPE | [6 empty] | 1/5
| 15 | DESIGN TEMPERATURE | [10 empty] | 85 |  |  |  |  | (ºC) | TEST PRESS. | [5 empty] | ATM + FULL OF WATER |  |  |  |  | (barg)
| 16 | DESIGN PRESSURE | [7 empty] | ATM + FULL OF WATER | [7 empty] | (barg) | WIND DESIGN |  | (ASCE7-10) |  |  |  | WIND SPEED |  |  | 232 |  | (Km/hr)
| 17 | MAX. ALLOWABLE WORKING PRESSURE | [10 empty] | (1) |  |  |  |  | (barg) | MIN./MAX. RECORDED AMB. TEMPERATURE | [7 empty] | 5 / |  | 50 | (ºC)
| 18 | SEISMIC DESIGN |  |  | ASCE 7-10 |  |  | SITE CLASS: |  |  | D | IMPORT. FACTOR: |  |  |  | 1.25 |  |  | EARTHING CONTINUITY | [7 empty] | YES
| 19 | Fa : 1 | Fv : 1.33 |  |  | Ss : 1.125 |  |  | S1 : 0.46 | [9 empty] | INSULATION | [7 empty] | No
| 20 | JOINT EFFICIENCY |  |  |  |  | 0.85
| 21 | FLANGE FACE FINISH |  |  |  |  | Ra 3.2 to 6.4 µm
| 22 | CORROSION ALLOWANCE SHEEL& BOTTOM / ROOF / STRUCTURE | [17 empty] | 1.6 / | 1.6 / | 1.6 | [7 empty] | (mm)
| 23 | Reference Codes and the Project Documents
| 24 | DESIGN CODE | [16 empty] | AWWA D-100 , IPS-G-ME-100
| 25 | SPECIFICATION FOR ATMOSPHERIC ABOVE GROUND WELDED STEEL TANKS | [16 empty] | BK-GNRAL-PEDCO-000-ME-SP-0002
| 26 | STANDARD DETAILS DRAWINGS FOR STORAGE TANKS | [16 empty] | BK-GNRAL-PEDCO-000-ME-DW-0002
| 27 | PROCESS BASIS OF DESIGN | [16 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
| 28 | STRUCTURAL DESIGN CRITERIA | [16 empty] | BK-GNRAL-PEDCO-000-ST-DC-0002
| 29 | SPECIFICATION FOR INSULATION | [16 empty] | BK-GENRAL-PEDCO-000-PI-SP-0019
| 30 | SPECIFICATION FOR PAINTING | [16 empty] | BK-GENRAL-PEDCO-000-PI-SP-0006
| 31 | P&ID | [16 empty] | BK-GCS-PEDCO-120-PR-PI-0024 (11)
| 32 | IPS Standard Drawing | [16 empty] | IPS-D-CE-412
| 34 | Materials
| 35 | SHELL/BOTTOM/ROOF : |  |  |  |  | A-283 Gr.C + Lining food grade (11) | [11 empty] | REINFORCING PAD: |  |  |  |  | A-283 Gr.C
| 36 | NOZZLE NECK PIPES : |  |  |  |  | A-106 Gr. B-Galvanaized | [11 empty] | INSUL. SUPPORT CLIP: |  |  |  |  | A-283 Gr.C
| 37 | FLANGES : |  |  |  |  | A-105-Galvanaized | [11 empty] | INTERNAL LADDER: |  |  |  |  | A-36 + Lining food grade (NOTE 11)
| 38 | FITTINGS : |  |  |  |  | A-234 Gr. WPB-Galvanaized | [11 empty] | EXTERNAL SUPPORTS: |  |  |  |  | A-283 Gr.C
| 39 | GASKETS : |  |  |  |  | NON-ASBESTOS , FLAT & GRAPHITE FILLED | [11 empty] | EXTERNAL BOLTS / NUTS: |  |  |  |  | A-193 Gr. B7 / SA-194 Gr. 2H
| 40 | ELECTRODES : |  |  |  |  | ACC. TO AWS | [11 empty] | EARTHING LUG / PLUG: |  |  |  |  | S.S.
| 41 | EXT. STRUCTURAL PIPE : |  |  |  |  | API 5L Gr. B / A53 Gr.B | [11 empty] | NAME PLATE/BRACKET: |  |  |  |  | S.S. 316 / C.S.
| 42 | CHECKERED PLATE : |  |  |  |  | ST-37 | [11 empty] | BASE PLATE : |  |  |  |  | ST-37
| 43 | ANCHOR BOLT : |  |  |  |  | A-307 Gr. B | [11 empty] | INT. REMOV. WETTED PARTS: |  |  |  |  | A-283 Gr.C + Lining food grade (NOTE 11)
| 45 | Lining : |  |  |  |  | P5 (Food Grade Epoxy)
| 46 | Surface Preparation & Coating
| 47 | TANK INTERIOR & EXTERIOR SURFACES | [16 empty] | YES ; ACC. TO SPECIFICATION NO.BK-GNRAL-PEDCO-000-PI-SP-0006 &
| 48 | [19 empty] | BK-GNRAL-PEDCO-000-PI-SP-0007 RESPECTIVELY.
| 49 | RELATED SUPPORTS & STRUCTURES : | [16 empty] | YES ; ACC. TO SPECIFICATIONS NO. BK-GNRAL-PEDCO-000-ST-DC-0001,
| 50 | [17 empty] | BK-GNRAL-PEDCO-000-ST-SP-0003, BK-GNRAL-PEDCO-000-ST-SP-0005.
51
| 52 | RISER PIPES(INLET, OUTLET,DRAIN & OVERFLOW),FLANGES & ELBOWS : | [16 empty] | SHALL BE GALVANIZED C.S. (11)
| 53 | ALL EXTERNAL BOLTS AND NUTS : | [16 empty] | SHALL BE GALVANIZED C.S.(11)
54
55
56
57
58
59
60
61
62
63
64

## TK-2209(2)
NISOC | [7 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MECHANICAL DATA SHEETS FOR ELEVATED POTABLE WATER TANK
شماره پیمان: | [7 empty] | پروژه |  | بسته کاری | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  |  | شماره صفحه: 5 از 6
9184 – 073 - 053 | [7 empty] | BK |  | GCS | PEDCO |  | 120 |  | ME |  | DT |  | 0011 |  | D04
Mech. Data Sheets for Elevated Potable Water Tank (TK-2209) / Sheet 5 of 6
Rev. | ACCESSORIES & NOZZLES LIST
| 1 | Accessories & Attachments (Note 11, 17)
| 2 | INTERNAL SUPPORTS | [11 empty] | YES |  |  | INTERNAL SHOT –BLASTING | [11 empty] | YES
| 3 | INTERNAL STAIRS | [11 empty] | YES |  |  | EXTERNAL SHOT –BLASTING | [11 empty] | YES
| 4 | SHOP ASSEMBLY | [11 empty] | YES |  |  | CLEANING AND PAINTING | [11 empty] | YES
| 5 | EXTERNAL PIPING SUPPORT | [11 empty] | YES |  |  | PICKLING AND PASSIVATION | [11 empty] | NO
| 6 | SUPPORTING | [11 empty] | YES |  |  | BLIND FLANGES, GASKETS, BOLTING | [11 empty] | YES
| 7 | LADDER, PLATFORM AND CLIPS | [11 empty] | YES |  |  | NAMEPLATE AND BRACKET | [11 empty] | YES
| 8 | INSULATION SUPPORTS | [11 empty] | YES |  |  | LIFTING TRUNNION | [11 empty] | NO
| 9 | INSULATION | [11 empty] | NO |  |  | LIFTING LUGS | [11 empty] | YES
| 10 | FIREPROOFING SUPPORT | [11 empty] | NO |  |  | EARTHING LUG & PLUG | [11 empty] | YES
| 11 | VORTEX BREAKER | [14 empty] | TAILING LUGS | [11 empty] | NO
12
13
| 14 | Nozzles List (Notes 1, 4, 5 & 26)*
| 15 | Mark |  |  | Qty. |  | Description |  |  |  |  | Pipe | [5 empty] | Flange |  |  |  |  | Proj. |  | Reinforcement |  |  | Remarks
| 16 | [10 empty] | Size |  | Thk.(mm) |  | Sch. |  | Type |  | Rate. | Face |  | (mm) |  | Thk. | O.D.
| 17 | A |  |  | 1 |  | Water Inlet |  |  |  |  | 2" | [5 empty] | WN |  | #150 | RF |  | See dwg
| 18 | B1 |  |  | 1 |  | Water Outlet |  |  |  |  | 2" | [5 empty] | WN |  | #150 | RF |  | See dwg
| 19 | B2 |  |  | 1 |  | Over Flow |  |  |  |  | 2" | [5 empty] | WN |  | #150 | RF |  | See dwg
| 20 | M1 |  |  | 1 |  | Manhole |  |  |  |  | 24" | [5 empty] | WN |  | #150 | RF |  | 2056 |  |  |  |  | Note 23
| 21 | L |  |  | 1 |  | Level Transmitter |  |  |  |  | 2" | [5 empty] | WN |  | #300 | RF |  | 1906
| 22 | D |  |  | 1 |  | Drain |  |  |  |  | 2" | [5 empty] | WN |  | #150 | RF |  | 1906
| 23 | V |  |  | 1 |  | Vent |  |  |  |  | 2" | [5 empty] | WN |  | #150 | RF | [6 empty] | With Wire Mesh Breather
24
25
26
27
28
29
30
| 31 | Wind and Seismic Loads at Base (Note 1)
| 32 |  |  | Load Condition |  | Empty Condition | [8 empty] | Operating Condition | [9 empty] | Testing Condition
33
| 34 |  |  |  |  | Max. Shear @ Base (Kg) |  |  | Max. Moment @ Base (Kg.m) |  |  | Weight (Kg) |  |  | Max. Shear @ Base (Kg) |  |  |  | Max. Moment @ Base (Kg.m) |  |  | Weight (Kg) |  |  | Max. Shear @ Base (Kg) |  | Max. Moment @ Base (Kg.m) |  | Weight (Kg)
35
| 36 |  | Load Type
37
38
| 39 | WIND
40
| 41 | SEISMIC
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63

## TK-2209(3)
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MECHANICAL DATA SHEETS FOR ELEVATED POTABLE WATER TANK
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 6 از 6
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | ME | DT | 0011 | D04
Mech. Data Sheets for Elevated Potable Water Tank (TK-2209) / Sheet 6 of 6
Sketch
MECHANICAL DATA SHEETS FOR ELEVATED POTABLE WATER TANK