## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0010 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2056 |  |  | Transmital Date: 5/1/2023
Document Title: Data Sheets For Power & Control Cables |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-2056 |  |  | Transmital Date: 5/1/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-DT-0010_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 |  |  | 1402-2294-92783 | 1402/03/09 | بازگشت به شماره نامه 03/2294/196117 به مورخ 1403/05/24 پاسخ ترانسمیتال TR-2487 ( مطابق با مدرک مبانی طراحی برق پروژه ، می بایست عایق کابلها در سطوح ولتاژی 3.3KV , 11KV به ترتیب 3.6/6KV , 12/20KV طراحی و تهیه گردد . لذا RATED VOLTAGE در نظر گرفته شده بر این اساس اصلاح گردد.) با توجه به کامنت اعلام شده در مدرک Calculation note for cable sizing مدرک دیتا شیت کابل به روز رسانی گردید.
2
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: