## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0010 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2056 |  |  | Transmital Date: 5/1/2023
Document Title: Data Sheets For Power & Control Cables |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-2056 |  |  | Transmital Date: 5/1/2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-DT-0010_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Page 3, Items 2.8&2.9: According to IPS-M-EL-272(2), clause 4.2, The rated voltages U0/U(Um) of the cables considered in this standard are as follows: U0/U(Um) = 6/10 (12) – 18/30 (36) kV, so items 2.8&2.9 shall be modified. |  | BK-SUR-ENG-ELE-00-03320 | 2022-03-05 | بر اساس استاندارد مذکور اصلاح گردید. |  |  | Noted and Closed.
2 | Page 3, Item 2.3: According to NISOC format SC shall be added to item 2.3. Meanwhile it has been considered in item 3.11. |  | BK-SUR-ENG-ELE-00-03320 | 2022-03-05 | در بند 2.3، Screen اضافه گردید. |  |  | Noted and Closed.
3 | Page 4, Item 3.23: Jacket color shall be modified to "Red" instead of "Black". |  | BK-SUR-ENG-ELE-00-03320 | 2022-03-05 | اصلاح گردید. |  |  | Noted and Closed.
4 | Page 5, Item 7: According to NISOC format partial discharge test shall be added. |  | BK-SUR-ENG-ELE-00-03320 | 2022-03-05 | اضافه گردید. |  |  | Noted and Closed.
5 | Reference document of quantity, length, number of drums, conductor cross section and number of cores shall be modified to"Cable Drum Schedule and Cutting List of Well Pads". |  | BK-SUR-ENG-ELE-00-03320 | 2022-03-05 | در زیر هر جدول به مدرک مشخصات فنی هر کابل اشاره شده است. |  |  | Noted and Closed.
6 | No Comment. |  | BK-SUR-ENG-ELE-01-04489 | 2022-05-30 | مورد تأیید است.
7 | No Comment. |  | BK-SUR-ENG-ELE-01-05114 | 2022-07-19 | مورد تأیید است.
8 | No Comment. |  | BK-SUR-ENG-ELE-02-07520 | 2023-05-01 | مدرک دیتا شیت کابل براساس نامه کارفرمای اصلی پروژه به شماره 03/2294/196117 بر روی ترانسمیتال 2487 روز رسانی گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: