## Cover Page
|  | Sari Pump Station Balance Tanks Fat Punch List Input/Output List |  | National Iranian Oil Engineering and Construction Company (NIOEC)
Control Sazan pooyande Co. |  | Iran Caspian Oil Transfer & Refining Project Sari Pump Station & Moghanak Terminal Balance Tanks Project |  | Page : 1 of 25 |  | Rev: B
Moghanak Pump Station Balance Tanks FAT Punch List Input/Output List
B | FAT Punch List |  | B.N | S.Shojaei | H.Khodam | 2014-03-10
A | Preliminary |  | Z.P | S.Shojaei | H.Khodam | 2012-07-15
Rev. | Description |  | Design | Check | Approv. | Date

## IO List
|  |  | Moghanak Pump Station Balance Tanks I/O Configuration List | [8 empty] | National Iranian Oil Engineering and Construction Company (NIOEC)
Control Sazan pooyande Co. |  |  | Iran Caspian Oil Transfer & Refining Project Sari Pump Station & Moghanak Terminal Balance Tanks Project | [8 empty] | Page : of | [9 empty] | Rev :B
ITEMS | TAG NO. | SERVICE | LOCATION | SIGNAL | JB | CABEL | CORE | WIRE | CONTROL PANEL | [7 empty] | FORCE TO CHECK |  |  |  |  | REMARK
|  |  |  | TYPE |  |  |  |  | STRIP | TERM. | INTERFACE |  | R / S | CARD & CH. | TERM. | ADDR. | LOW 0% | 50% | HIGH 100% | ALARM | EVENT
1 | LIT-5180A | Balance TK-506A | F | AI (I-2W) | AJB-525 | C-5352 | 13 PAIR | 1,2,Sh | X112 | 1,2,Sh | BR 11-1 | CH1 | 3/7 | AI 1. 1 | 2, 3 | PIW 612
[12 empty] | CH2 | 4/6 | AI 1R. 1 | 2, 3 | PIW 708
2 | LIT-5180B | Balance TK-506B | F | AI (I-2W) | AJB-527 | C-5367 | 13 PAIR | 1,2,Sh | X113 | 1,2,Sh | BR 11-2 | CH1 | 3/7 | AI 1. 2 | 4, 5 | PIW 614
[12 empty] | CH2 | 4/6 | AI 1R. 2 | 4, 5 | PIW 710
3 | PIT-5181 | Discharg of Booster Pumps Pressure Transmitter | F | AI (I-2W) | AJB-531 | C-5399 | 6 Pair | 3,4,sh | X114 | 1,2,Sh | BR 11-3 | CH1 | 3/7 | AI 1. 3 | 6, 7 | PIW 616
[12 empty] | CH2 | 4/6 | AI 1R. 3 | 6, 7 | PIW 712
4 |  | Spare | F | AI (I-2W) | [8 empty] | 3/7 | AI 1. 4 | 8, 9 | PIW 618
[13 empty] | 4/6 | AI 1R. 4 | 8, 9 | PIW 714
5 |  | Spare | F | AI (I-2W) | [8 empty] | 3/7 | AI 1. 5 | 16, 17 | PIW 620
[13 empty] | 4/6 | AI 1R. 5 | 16, 17 | PIW 716
6 |  | Spare | F | AI (I-2W) | [8 empty] | 3/7 | AI 1. 6 | 12, 13 | PIW 622
[13 empty] | 4/6 | AI 1R. 6 | 12, 13 | PIW 718
7 |  | Spare | F | AI | [8 empty] | 3/7 | AI 1. 7 | 14, 15 | PIW 624
[13 empty] | 4/6 | AI 1R. 7 | 14, 15 | PIW 720
8 |  | Spare | F | AI | [8 empty] | 3/7 | AI 1. 8 | 18, 19 | PIW 626
[13 empty] | 4/6 | AI 1.R 8 | 18, 19 | PIW 722
9 | LIT-5440A | Diesel Line of fuel GG-501A | F | AI (I-2W) | AJB-523 | C-5342 | 13 PAIR | 1,2,Sh | X111 | 1,2,Sh | BR 12-1 | CH1 | 3/5 | AI 2. 1 | 2, 3 | PIW 628
10 | LIT-5440B | Diesel Line of fuel GG-501B | F | AI (I-2W) | AJB-523 | C-5342 | 13 PAIR | 3,4,Sh | X111 | 3,4,Sh | BR 12-2 | CH1 | 3/5 | AI 2. 2 | 4, 5 | PIW 630
11 | LIT-5440C | Diesel Line of fuel GG-501C | F | AI (I-2W) |  |  |  |  | X115 | 1,2,Sh | BR 12-3 | CH1 | 3/5 | AI 2. 3 | 6, 7 | PIW 632
12 | PIT-5180 | Inlet Line of Balance TK-506A/B | F | AI (I-2W) | AJB-533 | C-53104 | 13 Pair | 3,4,Sh | X115 | 3,4,Sh | BR 12-4 | CH1 | 3/5 | AI 2. 4 | 8, 9 | PIW 634
13 | TT-5180A | Balance TK-506A | F | AI (I-2W) | AJB-525 | C-5352 | 13 PAIR | 3,4,Sh | X112 | 3,4,Sh | BR 12-5 | CH1 | 3/5 | AI 2. 5 | 12, 13 | PIW 636
14 | TT-5180B | Balance TK-506B | F | AI (I-2W) | AJB-527 | C-5367 | 13 PAIR | 3,4,Sh | X113 | 3,4,Sh | BR 12-6 | CH1 | 3/5 | AI 2. 6 | 14, 15 | PIW 638
15 | FT-5180 | Inlert Line of Balance TK-506A/B | F | AI (I-2W) | AJB-533 | C-53104 | 6 Pair | 5,6,Sh | X113 | 5,6,Sh | BR 12-7 | CH1 | 3/5 | AI 2. 7 | 16, 17 | PIW 640
16 | FT-5181 | Discharg of Booster Pumps Flow Transmitter | F | AI (I-2W) | AJB-533 | C-53104 | 6 Pair | 7,8,Sh | X113 | 7,8,Sh | BR 12-8 | CH1 | 3/5 | AI 2. 8 | 18, 19 | PIW 642
17 |  | Spare | F | AI (I-2W) | [8 empty] | 3/6 | AI 3. 1 | 2, 3 | PIW 644
18 |  | Spare | F | AI (I-2W) | [8 empty] | 3/6 | AI 3. 2 | 4, 5 | PIW 646
19 |  | Spare | F | AI (I-2W) | [8 empty] | 3/6 | AI 3. 3 | 6, 7 | PIW 648
20 |  | Spare | F | AI (I-2W) | [8 empty] | 3/6 | AI 3. 4 | 8, 9 | PIW 650
21 |  | Spare | F | AI (I-2W) | [8 empty] | 3/6 | AI 3. 5 | 12, 13 | PIW 652
22 |  | Spare | F | AI (I-2W) | [8 empty] | 3/6 | AI 3. 6 | 14, 15 | PIW 654
23 |  | Spare | F | AI (I-2W) | [8 empty] | 3/6 | AI 3. 7 | 16, 17 | PIW 656
24 |  | Spare | F | AI (I-2W) | [8 empty] | 3/6 | AI 3. 8 | 18, 19 | PIW 658
25 |  | Spare | F | AI (I-2W) | [8 empty] | 3/7 | AI 4. 1 | 2, 3 | PIW 660
26 | PIT-5805 | At Farthest fire water service Pressure | F | AI (I-2W) |  |  |  |  | X119 | 5,6,Sh | - | - | 3/7 | AI 4. 2 | 4, 5 | PIW 662
27 | II- IN.1-512 | MCC 512-IN.1 CURRENT VALUE | MCC 512 | AI (I-2W) | MCC 512 | C-53122 | 1 Pair | 1,2,Sh | X11A | 5,6,Sh | - | - | 3/7 | AI 4. 3 | 6, 7 | PIW 664
28 | II- IN.2-512 | MCC 512-IN.2 CURRENT VALUE | MCC 512 | AI (I-2W) | MCC 512 | C-53123 | 1 Pair | 1,2,Sh | X11A | 7,8,Sh | - | - | 3/7 | AI 4. 4 | 8, 9 | PIW 666
29 | TT-5190 | Temp Boiler | MCC 512 | AI (I-2W) |  |  |  |  | X11A | 9,10,Sh | - | - | 3/7 | AI 4. 5 | 12, 13 | PIW 668
30 | LIT-5801A | Fire Fighting Storage TK-505A | MCC 512 | AI (I-2W) |  |  |  |  | X119 | 1,2,Sh | - | - | 3/7 | AI 4. 6 | 14, 15 | PIW 670
31 | LIT-5801B | Fire Fighting Storage TK-505B | MCC 512 | AI (I-2W) |  |  |  |  | X119 | 3,4,Sh | - | - | 3/7 | AI 4. 7 | 16, 17 | PIW 672
32 | LIT-5701 |  | MCC 512 | AI (I-2W) |  |  |  |  | X119 | 7,8,Sh | - | - | 3/7 | AI 4. 8 | 18, 19 | PIW 674
33 |  | Hot Spare | MCC 511 | AI (I-2W) | MCC 511 | C-53124 | 1 Pair | 1,2,Sh | X11B | 1,2,Sh | - | - | 3/8 | AI 5. 1 | 2, 3 | PIW 676
34 | II-P-511B | P-M-511/ B Booster P-511B Curreant Value | MCC 511 | AI (I-2W) | MCC 511 | C-53125 | 1 Pair | 1,2,Sh | X11B | 3,4,Sh | - | - | 3/8 | AI 5. 2 | 4, 5 | PIW 678
35 | II-P-511C | P-M-511/ C Booster P-511C Curreant Value | MCC 511 | AI (I-2W) |  |  |  |  | X11B | 5,6,Sh | - | - | 3/8 | AI 5. 3 | 6, 7 | PIW 680
36 | II-P-511D | P-M-511/ D Booster P-511D Curreant Value | MCC 511 | AI (I-2W) | MCC 511 | C-53127 | 1 Pair | 1,2,Sh | X11B | 7,8,Sh | - | - | 3/8 | AI 5. 4 | 8, 9 | PIW 682
37 | II-P-511E | P-M-511/ E Booster P-511E Curreant Value | MCC 511 | AI (I-2W) | MCC 511 | C-53128 | 1 Pair | 1,2,Sh | X11B | 9,10,Sh | - | - | 3/8 | AI 5. 5 | 12, 13 | PIW 684
38 | II- IN.1-511 | MCC 511-IN.1 CURRENT VALUE | MCC 511 | AI (I-2W) | MCC 511 | C-53120 | 1 Pair | 1,2,Sh | X11A | 1,2,Sh |  |  | 3/8 | AI 5. 6 | 14, 15 | PIW 686
39 | II- IN.2-511 | MCC 511-IN.2 CURRENT VALUE | MCC 511 | AI (I-2W) | MCC 511 | C-53121 | 1 Pair | 1,2,Sh | X11A | 3,4,Sh |  |  | 3/8 | AI 5. 7 | 16, 17 | PIW 688
40 | II-P-511A | P-M-511/A Booster P-511ACurreant Value | MCC 511 | AI (I-2W) |  |  |  |  | X11B | 11,12,Sh | - | - | 3/8 | AI 5. 8 | 18, 19 | PIW 690
41 | TE-5181A | Booster P-511A Pump DE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X121 | 1,2,3,Sh | BR 13-1 | CH1 | 3/9 | AI 6. 1 | 2, 3 | PIW 692
42 | TE-5182A | Booster P-511A Pump NDE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X121 | 4,5,6,Sh | BR 13-1 | CH2 | 3/9 | AI 6. 2 | 4, 5 | PIW 694
43 | TE-5183A | Booster P-511A Motor DE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X121 | 7,8,9,Sh | BR 13-2 | CH1 | 3/9 | AI 6. 3 | 6, 7 | PIW 696
44 | TE-5184A | Booster P-511A Motor NDE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X121 | 10,11,12,Sh | BR 13-2 | CH2 | 3/9 | AI 6. 4 | 8, 9 | PIW 698
45 | TE-5185A | Booster P-511A Motor Winding#1 Temperature High | F | AI (RTD) |  |  |  |  | X121 | 13,14,15,Sh | BR 13-3 | CH1 | 3/9 | AI 6. 5 | 12, 13 | PIW 700
46 | TE-5186A | Booster P-511A Motor Winding#2 Temperature High | F | AI (RTD) |  |  |  |  | X121 | 16,17,18,Sh | BR 13-3 | CH2 | 3/9 | AI 6. 6 | 14, 15 | PIW 702
47 | TE-5187A | Booster P-511A Motor Winding#3 Temperature High | F | AI (RTD) |  |  |  |  | X121 | 19,20,21,Sh | BR 13-4 | CH1 | 3/9 | AI 6. 7 | 16, 17 | PIW 704
48 |  | Hot Spare | F | AI (RTD) |  |  |  |  | X121 | 22,23,24,Sh | BR 13-4 | CH2 | 3/9 | AI 6. 8 | 18, 19 | PIW 706
49 | TE-5181B | Booster P-511B Pump DE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X122 | 1,2,3,Sh | BR 14-1 | CH1 | 4/7 | AI 7. 1 | 2, 3 | PIW 724
50 | TE-5182B | Booster P-511B Pump NDE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X122 | 4,5,6,Sh | BR 14-1 | CH2 | 4/7 | AI 7. 2 | 4, 5 | PIW 726
51 | TE-5183B | Booster P-511B Motor DE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X122 | 7,8,9,Sh | BR 14-2 | CH1 | 4/7 | AI 7. 3 | 6, 7 | PIW 728
52 | TE-5184B | Booster P-511B Motor NDE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X122 | 10,11,12,Sh | BR 14-2 | CH2 | 4/7 | AI 7. 4 | 8, 9 | PIW 730
53 | TE-5185B | Booster P-511B Motor Winding#1 Temperature High | F | AI (RTD) |  |  |  |  | X122 | 13,14,15,Sh | BR 14-3 | CH1 | 4/7 | AI 7. 5 | 12, 13 | PIW 732
54 | TE-5186B | Booster P-511B Motor Winding#2 Temperature High | F | AI (RTD) |  |  |  |  | X122 | 16,17,18,Sh | BR 14-3 | CH2 | 4/7 | AI 7. 6 | 14, 15 | PIW 734
55 | TE-5187B | Booster P-511B Motor Winding#3 Temperature High | F | AI (RTD) |  |  |  |  | X122 | 19,20,21,Sh | BR 14-4 | CH1 | 4/7 | AI 7. 7 | 16, 17 | PIW 736
56 |  | Hot Spare | F | AI (RTD) |  |  |  |  | X122 | 22,23,24,Sh | BR 14-4 | CH2 | 4/7 | AI 7. 8 | 18, 19 | PIW 738
57 | TE-5181C | Booster P-511C Pump DE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X123 | 1,2,3,Sh | BR 15-1 | CH1 | 4/8 | AI 8. 1 | 2, 3 | PIW 740
58 | TE-5182C | Booster P-511C Pump NDE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X123 | 4,5,6,Sh | BR 15-1 | CH2 | 4/8 | AI 8. 2 | 4, 5 | PIW 742
59 | TE-5183C | Booster P-511C Motor DE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X123 | 7,8,9,Sh | BR 15-2 | CH1 | 4/8 | AI 8. 3 | 6, 7 | PIW 744
60 | TE-5184C | Booster P-511C Motor NDE BeCring Temperature High | F | AI (RTD) |  |  |  |  | X123 | 10,11,12,Sh | BR 15-2 | CH2 | 4/8 | AI 8. 4 | 8, 9 | PIW 746
61 | TE-5185C | Booster P-511C Motor Winding#1 Temperature High | F | AI (RTD) |  |  |  |  | X123 | 13,14,15,Sh | BR 15-3 | CH1 | 4/8 | AI 8. 5 | 12, 13 | PIW 748
62 | TE-5186C | Booster P-511C Motor Winding#2 Temperature High | F | AI (RTD) |  |  |  |  | X123 | 16,17,18,Sh | BR 15-3 | CH2 | 4/8 | AI 8. 6 | 14, 15 | PIW 750
63 | TE-5187C | Booster P-511C Motor Winding#3 Temperature High | F | AI (RTD) |  |  |  |  | X123 | 19,20,21,Sh | BR 15-4 | CH1 | 4/8 | AI 8. 7 | 16, 17 | PIW 752
64 | TE-5183E | Booster P-511E Motor DE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X123 | 28,29,30,Sh | BR 15-4 | CH2 | 4/8 | AI 8. 8 | 18, 19 | PIW 754
65 |  | Hot Spare | F | AI (RTD) |  |  |  |  | X124 | 1,2,3,Sh | BR 16-1 | CH1 | 4/9 | AI 9. 1 | 2, 3 | PIW 756
66 | TE-5182D | Booster P-511C Pump NDE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X124 | 4,5,6,Sh | BR 16-1 | CH2 | 4/9 | AI 9. 2 | 4, 5 | PIW 758
67 | TE-5183D | Booster P-511D Motor DE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X124 | 7,8,9,Sh | BR 16-2 | CH1 | 4/9 | AI 9. 3 | 6, 7 | PIW 760
68 | TE-5184D | Booster P-511D Motor NDE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X124 | 10,11,12,Sh | BR 16-2 | CH2 | 4/9 | AI 9. 4 | 8, 9 | PIW 762
69 | TE-5185D | Booster P-511D Motor Winding#1 Temperature High | F | AI (RTD) |  |  |  |  | X124 | 13,14,15,Sh | BR 16-3 | CH1 | 4/9 | AI 9. 5 | 12, 13 | PIW 764
70 | TE-5186D | Booster P-511D Motor Winding#2 Temperature High | F | AI (RTD) |  |  |  |  | X124 | 16,17,18,Sh | BR 16-3 | CH2 | 4/9 | AI 9. 6 | 14, 15 | PIW 766
71 | TE-5187D | Booster P-511D Motor Winding#3 Temperature High | F | AI (RTD) |  |  |  |  | X124 | 19,20,21,Sh | BR 16-4 | CH1 | 4/9 | AI 9. 7 | 16, 17 | PIW 768
72 | TE-5181D | Booster P-511C Pump DE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X124 | 22,23,24,Sh | BR 16-4 | CH2 | 4/9 | AI 9. 8 | 18, 19 | PIW 770
73 |  | Hot Spare | F | AI (RTD) |  |  |  |  | X125 | 1,2,3,Sh | BR 17-1 | CH1 | 4/10 | AI 10. 1 | 2, 3 | PIW 772
| TE-5182E | Booster P-511E Pump NDE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X125 | 4,5,6,Sh | BR 17-1 | CH2 | 4/10 | AI 10. 2 | 4, 5 | PIW 774
74 |  | Hot Spare | F | AI (RTD) |  |  |  |  | X125 | 7,8,9,Sh | BR 17-2 | CH1 | 4/10 | AI 10. 3 | 6, 7 | PIW 776
| TE-5184E | Booster P-511E Motor NDE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X125 | 10,11,12,Sh | BR 17-2 | CH2 | 4/10 | AI 10. 4 | 8, 9 | PIW 778
75 | TE-5185E | Booster P-511E Motor Winding#1 Temperature High | F | AI (RTD) |  |  |  |  | X125 | 13,14,15,Sh | BR 17-3 | CH1 | 4/10 | AI 10. 5 | 12, 13 | PIW 780
76 | TE-5186E | Booster P-511E Motor Winding#2 Temperature High | F | AI (RTD) |  |  |  |  | X125 | 16,17,18,Sh | BR 17-3 | CH2 | 4/10 | AI 10. 6 | 14, 15 | PIW 782
77 | TE-5187E | Booster P-511E Motor Winding#3 Temperature High | F | AI (RTD) |  |  |  |  | X125 | 19,20,21,Sh | BR 17-4 | CH1 | 4/10 | AI 10. 7 | 16, 17 | PIW 784
78 | TE-5181E | Booster P-511E Pump DE Bearing Temperature High | F | AI (RTD) |  |  |  |  | X125 | 22,23,24,Sh | BR 17-4 | CH2 | 4/10 | AI 10. 8 | 18, 19 | PIW 786
79 | LSH-5801A | Fire Fighting Storage TK-505A Level High | FF | DI | DJB-520 | C-5306 | 20 Core | 1,2 | X131 | 1,2 | - | - | 3/4 | DI 1. 1 | 2 | I 100.0
80 | LSL-5801A | Fire Fighting Storage TK-505A Level Low | FF | DI | DJB-520 | C-5306 | 20 Core | 3,4 | X131 | 3,4 | - | - | 3/4 | DI 1. 2 | 3 | I 100.1
81 | LSLL-5801A | Fire Fighting Storage TK-505A Level Low Low | FF | DI | DJB-520 | C-5306 | 20 Core | 5,6 | X131 | 5,6 | - | - | 3/4 | DI 1. 3 | 4 | I 100.2
82 | LSH-5801B | Fire Fighting Storage TK-505B Level High | FF | DI | DJB-520 | C-5306 | 20 Core | 7,8 | X131 | 7,8 | - | - | 3/4 | DI 1. 4 | 5 | I 100.3
83 | LSL-5801B | Fire Fighting Storage TK-505B Level Low | FF | DI | DJB-520 | C-5306 | 20 Core | 9,10 | X131 | 9,10 | - | - | 3/4 | DI 1. 5 | 6 | I 100.4
84 | LSHH-5801B | Fire Fighting Storage TK-505B Level High High | FF | DI | DJB-520 | C-5306 | 20 Core | 11,12 | X131 | 11,12 | - | - | 3/4 | DI 1. 6 | 7 | I 100.5
85 | LSL-5441A | Diesel fire DailyTank GG-502A Level Low | FF | DI | DJB-526 | C-5339 | 20 Core | 11,12 | X131 | 13,14 | - | - | 3/4 | DI 1. 7 | 8 | I 100.6
86 | LSL-5441B | Diesel fire DailyTank GG-502B Level Low | FF | DI | DJB-526 | C-5339 | 20 Core | 13,14 | X131 | 15,16 | - | - | 3/4 | DI 1. 8 | 9 | I 100.7
87 | LSL-5441C | Diesel fire DailyTank GG-502C Level Low | FF | DI |  |  |  |  | X131 | 17,18 | - | - | 3/4 | DI 1. 9 | 12 | I 101.0
88 | P-506C- Fault | Elec.P-506C Fault | FF | DI |  |  |  |  | X131 | 19,20 | - | - | 3/4 | DI 1. 10 | 13 | I 101.1
89 | P-506C- Run | Elec.P-506C Running | FF | DI |  |  |  |  | X131 | 21,22 | - | - | 3/4 | DI 1. 11 | 14 | I 101.2
90 |  | Hot Spare | FF | DI |  |  |  |  | X131 | 23,24 | - | - | 3/4 | DI 1. 12 | 15 | I 101.3
91 |  | Hot Spare | FF | DI |  |  |  |  | X131 | 25,26 | - | - | 3/4 | DI 1. 13 | 16 | I 101.4
92 | P-506A -Fault | Diesel P-506A Fault | FF | DI |  |  |  |  | X131 | 27,28 | - | - | 3/4 | DI 1. 14 | 17 | I 101.5
93 | P-506A- Run | Diesel P-506A Running | FF | DI |  |  |  |  | X131 | 29,30 | - | - | 3/4 | DI 1. 15 | 18 | I 101.6
94 | P-506B -Fault | Diesel P-506B Fault | FF | DI |  |  |  |  | X131 | 31,32 | - | - | 3/4 | DI 1. 16 | 19 | I 101.7
95 | P-506B- Run | Diesel P-506B Running | FF | DI |  |  |  |  | X131 | 33,34 | - | - | 3/4 | DI 1. 17 | 22 | I 102.0
96 | P-507A -Fault | Jockey P-507A Fault | FF | DI |  |  |  |  | X131 | 35,36 | - | - | 3/4 | DI 1. 18 | 23 | I 102.1
97 | P-507A- Run | Jockey P-507A Running | FF | DI |  |  |  |  | X131 | 37,38 | - | - | 3/4 | DI 1. 19 | 24 | I 102.2
98 | P-507B -Fault | Jockey P-507B Fault | FF | DI |  |  |  |  | X131 | 39,40 | - | - | 3/4 | DI 1. 20 | 25 | I 102.3
99 | P-507B- Run | Jockey P-507B Running | FF | DI |  |  |  |  | X131 | 41,42 | - | - | 3/4 | DI 1. 21 | 26 | I 102.4
100 | PSH-5801 | Jockey Pumps P-507A/B Press. High | FF | DI | - | C-5313 | 2 Core |  | X131 | 43,44 | - | - | 3/4 | DI 1. 22 | 27 | I 102.5
101 | PSL-5802 | Jockey Pumps P-507A/B Press. Low | FF | DI | - | C-5314 | 2 Core |  | X131 | 45,46 | - | - | 3/4 | DI 1. 23 | 28 | I 102.6
102 | PSL-5804A | Outlet Diesel P-5060A Press. Low | FF | DI | - | C-5311 | 2 Core |  | X131 | 47,48 | - | - | 3/4 | DI 1. 24 | 29 | I 102.7
103 | PSL-5804B | Outlet Diesel P-506B Press. Low | FF | DI | - | C-5312 | 2 Core |  | X131 | 49,50 | - | - | 3/4 | DI 1. 25 | 32 | I 103.0
104 | PSL-5803A | Outlet Elec.P-505A Press. Low | FF | DI | - | C-5309 | 2 Core |  | X131 | 51,52 | - | - | 3/4 | DI 1. 26 | 33 | I 103.1
105 | PSL-5803B | Outlet Elec.P-505B Press. Low | FF | DI | - | C-5310 | 2 Core |  | X131 | 53,54 | - | - | 3/4 | DI 1. 27 | 34 | I 103.2
106 |  | Hot Spare | FF | DI |  |  |  |  | X131 | 55,56 | - | - | 3/4 | DI 1. 28 | 35 | I 103.3
107 |  | Hot Spare | FF | DI |  |  |  |  | X131 | 57,58 | - | - | 3/4 | DI 1. 29 | 36 | I 103.4
108 |  | Hot Spare | FF | DI |  |  |  |  | X131 | 59,60 | - | - | 3/4 | DI 1. 30 | 37 | I 103.5
109 |  | Spare | FF | DI | [8 empty] | 3/4 | DI 1. 31 | 38 | I 103.6
110 |  | Spare | FF | DI | [8 empty] | 3/4 | DI 1. 32 | 39 | I 103.7
111 | ZLO-5804A | MOV-5804A Opened position | F&G | DI | DJB-522A |  | 20 Core | 7,8 | X132 | 1,2 | - | - | 4/4 | DI 2. 1 | 2 | I 104.0
112 | ZLC-5804A | MOV-5804A Closed position | F&G | DI | DJB-522A |  | 20 Core | 9,10 | X132 | 3,4 | - | - | 4/4 | DI 2. 2 | 3 | I 104.1
113 |  | Hot Spare | F&G | DI | DJB-522B |  | 20 Core | 11,12 | X132 | 5,6 | - | - | 4/4 | DI 2. 3 | 4 | I 104.2
114 | ZLO-5804B | MOV-5804B Opened position | F&G | DI | DJB-522B |  | 20 Core | 7,8 | X132 | 7,8 | - | - | 4/4 | DI 2. 4 | 5 | I 104.3
115 | ZLC-5804B | MOV-5804B Closed position | F&G | DI | DJB-522B |  | 20 Core | 9,10 | X132 | 9,10 | - | - | 4/4 | DI 2. 5 | 6 | I 104.4
116 | ZLC-5801A | Delug DV-5801A Closed Position | F&G | DI | DJB-522B |  | 20 Core | 13,14 | X132 | 11,12 | - | - | 4/4 | DI 2. 6 | 7 | I 104.5
117 | ZLO-5801A | Delug DV-5801A Opened Position | F&G | DI | DJB-522B |  | 20 Core | 15,16 | X132 | 13,14 | - | - | 4/4 | DI 2. 7 | 8 | I 104.6
118 | ZLC-5801B | Delug DV-5801B Closed Position | F&G | DI | DJB-522B |  | 20 Core | 17,18 | X132 | 15,16 | - | - | 4/4 | DI 2. 8 | 9 | I 104.7
119 | ZLO-5801B | Delug DV-5801B Opened Position | F&G | DI | DJB-522B |  | 20 Core | 19,20 | X132 | 17,18 | - | - | 4/4 | DI 2. 9 | 12 | I 105.0
120 | ZLC-5802A | Delug DV-5802A Closed Position | F&G | DI | DJB-524 | C-5326 | 20 Core | 1,2 | X132 | 19,20 | - | - | 4/4 | DI 2. 10 | 13 | I 105.1
121 | ZLO-5802A | Delug DV-5802A Opened Position | F&G | DI | DJB-524 | C-5326 | 20 Core | 3,4 | X132 | 21,22 | - | - | 4/4 | DI 2. 11 | 14 | I 105.2
122 | ZLC-5802B | Delug DV-5802B Closed Position | F&G | DI | DJB-524 | C-5326 | 20 Core | 5,6 | X132 | 23,24 | - | - | 4/4 | DI 2. 12 | 15 | I 105.3
123 | ZLO-5802B | Delug DV-5802B Opened Position | F&G | DI | DJB-524 | C-5326 | 20 Core | 7,8 | X132 | 25,26 | - | - | 4/4 | DI 2. 13 | 16 | I 105.4
124 | ZLC-5803A | Delug DV-5803A Closed Position | F&G | DI | DJB-524 | C-5326 | 20 Core | 9,10 | X132 | 27,28 | - | - | 4/4 | DI 2. 14 | 17 | I 105.5
125 | ZLO-5803A | Delug DV-5803A Opened Position | F&G | DI | DJB-524 | C-5326 | 20 Core | 11,12 | X132 | 29,30 | - | - | 4/4 | DI 2. 15 | 18 | I 105.6
126 | ZLC-5803B | Delug DV-5803B Closed Position | F&G | DI | DJB-524 | C-5326 | 20 Core | 13,14 | X132 | 31,32 | - | - | 4/4 | DI 2. 16 | 19 | I 105.7
127 | ZLO-5803B | Delug DV-5803B Opened Position | F&G | DI | DJB-524 | C-5326 | 20 Core | 15,16 | X132 | 33,34 | - | - | 4/4 | DI 2. 17 | 22 | I 106.0
128 | LSL-5802 | Concentration Foam StorageTank FG-502 Level Low | F&G | DI | DJB-522A |  | 20 Core | 13,14 | X132 | 35,36 | - | - | 4/4 | DI 2. 18 | 23 | I 106.1
129 | YL-5801A | Foam P-503A Fault | F&G | DI |  |  |  |  | X132 | 37,38 | - | - | 4/4 | DI 2. 19 | 24 | I 106.2
130 | YI-5801A | Foam P-503A Running | F&G | DI |  |  |  |  | X132 | 39,40 | - | - | 4/4 | DI 2. 20 | 25 | I 106.3
131 | YL-5801B | Foam P-503B Fault | F&G | DI |  |  |  |  | X132 | 41,42 | - | - | 4/4 | DI 2. 21 | 26 | I 106.4
132 | YI-5801B | Foam P-503B Running | F&G | DI |  |  |  |  | X132 | 43,44 | - | - | 4/4 | DI 2. 22 | 27 | I 106.5
133 |  | Hot Spare | F&G | DI |  |  |  |  | X132 | 45,46 | - | - | 4/4 | DI 2. 23 | 28 | I 106.6
134 |  | Hot Spare | F&G | DI |  |  |  |  | X132 | 47,48 | - | - | 4/4 | DI 2. 24 | 29 | I 106.7
135 |  | Spare | F&G | DI | [8 empty] | 4/4 | DI 2. 25 | 32 | I 107.0
136 |  | Spare | F&G | DI | [8 empty] | 4/4 | DI 2. 26 | 33 | I 107.1
137 |  | Spare | F&G | DI | [8 empty] | 4/4 | DI 2. 27 | 34 | I 107.2
138 |  | Spare | F&G | DI | [8 empty] | 4/4 | DI 2. 28 | 35 | I 107.3
139 |  | Spare | F&G | DI | [8 empty] | 4/4 | DI 2. 29 | 36 | I 107.4
140 |  | Spare | F&G | DI | [8 empty] | 4/4 | DI 2. 30 | 37 | I 107.5
141 |  | Spare | F&G | DI | [8 empty] | 4/4 | DI 2. 31 | 38 | I 107.6
142 |  | Spare | F&G | DI | [8 empty] | 4/4 | DI 2. 32 | 39 | I 107.7
143 | LSH-5440A | Diesel fuel GG-501A Level High | F | DI (N.C.) | DJB-526 | C-5339 | 20 Core | 1,2 | X211 | 1,2 | - | - | 5/4 | DI 3. 1 | 2 | I 108.0
144 | LSL-5440A | Diesel fuel GG-501A Level Low | F | DI (N.C.) | DJB-526 | C-5339 | 20 Core | 3,4 | X211 | 3,4 | - | - | 5/4 | DI 3. 2 | 3 | I 108.1
145 | LSH-5440B | Diesel fuel GG-501B Level High | F | DI (N.C.) | DJB-526 | C-5339 | 20 Core | 5,6 | X211 | 5,6 | - | - | 5/4 | DI 3. 3 | 4 | I 108.2
146 | LSL-5440B | Diesel fuel GG-501B Level Low | F | DI (N.C.) | DJB-526 | C-5339 | 20 Core | 7,8 | X211 | 7,8 | - | - | 5/4 | DI 3. 4 | 5 | I 108.3
147 | FSL-5440 | Outlet Diesel fuel P-504 Flow Low | F | DI (N.C.) | DJB-526 | C-5339 | 20 Core | 9,10 | X211 | 9,10 | - | - | 5/4 | DI 3. 5 | 6 | I 108.4
148 | LSHH-5180A | Balance TK-506A Level High High | F/ESD | DI | DJB-528 | C-5347 | 20 Core | 1,2 | X212 | 1,2 | IR 24-3 | - | 5/4 | DI 3. 6 | 7 | I 108.5
149 | LSH-5180A | Balance TK-506A Level High | F | DI (N.C.) | DJB-528 | C-5347 | 20 Core | 3,4 | X212 | 3,4 | - | - | 5/4 | DI 3. 7 | 8 | I 108.6
150 | LSL-5180A | Balance TK-506A Level Low | F | DI (N.C.) | DJB-530 | C-2356 | 20 Core | 1,2 | X212 | 5,6 | - | - | 5/4 | DI 3. 8 | 9 | I 108.7
151 | LSLL-5180A | Balance TK-506A Level LowLow | F | DI (N.C.) | DJB-530 | C-2356 | 20 Core | 3,4 | X212 | 7,8 | - | - | 5/4 | DI 3. 9 | 12 | I 109.0
152 | XA-5800 | Balance TK-506A/B Fire Alarm | ESD | DI | DJB-530 | C-2356 | 20 Core | 5,6 | X215 | 1,2 | IR 24-2 | - | 5/4 | DI 3. 10 | 13 | I 109.1
153 | SS-5181A | MOV-5181A Select in Remote | F | DI(N.O.) | DJB-528 | C-5347 | 20 Core | 5,6 | X213 | 5,6 | - | - | 5/4 | DI 3. 11 | 14 | I 109.2
154 | ZSO-5181A | MOV-5181 Opened Position | F | DI(N.O.) | DJB-528 | C-5347 | 20 Core | 11,12 | X213 | 7,8 | - | - | 5/4 | DI 3. 12 | 15 | I 109.3
155 | ZSC-5181A | MOV-5181A Closed Position | F | DI(N.O.) | DJB-528 | C-5347 | 20 Core | 13,14 | X213 | 9,10 | - | - | 5/4 | DI 3. 13 | 16 | I 109.4
156 |  | Hot Spare | F | DI | DJB-528 | C-5347 | 20 Core | 15,16 | X213 | 11,12 | - | - | 5/4 | DI 3. 14 | 17 | I 109.5
157 | SS-5181B | MOV-5181B Select in Remote | F | DI(N.O.) | DJB-532A |  | 20 Core | 9,10 | X213 | 17,18 | - | - | 5/4 | DI 3. 15 | 18 | I 109.6
158 | ZSC-5181B | MOV-5181B Closed Position | F | DI(N.O.) | DJB-532A |  | 20 Core | 13,14 | X213 | 19,20 | - | - | 5/4 | DI 3. 16 | 19 | I 109.7
159 | ZSO-5181B | MOV-5181B Opened Position | F | DI(N.O.) | DJB-532A |  | 20 Core | 11,12 | X213 | 21,22 | - | - | 5/4 | DI 3. 17 | 22 | I 110.0
160 |  | Hot Spare | F | DI | DJB-532A |  | 20 Core | 15,16 | X213 | 23,24 | - | - | 5/4 | DI 3. 18 | 23 | I 110.1
161 | ZSC-5182B | MOV-5182B Closed Position | F | DI(N.O.) | DJB-532B |  | 20 Core | 13,14 | X213 | 29,30 | - | - | 5/4 | DI 3. 19 | 24 | I 110.2
162 | ZSO-5182B | MOV-5182B Opened Position | F | DI(N.O.) | DJB-532B |  | 20 Core | 11,12 | X213 | 31,32 | - | - | 5/4 | DI 3. 20 | 25 | I 110.3
163 | SS-5182B | MOV-5182B Select in Remote | F | DI(N.O.) | DJB-532B |  | 20 Core | 9,10 | X213 | 33,34 | - | - | 5/4 | DI 3. 21 | 26 | I 110.4
164 |  | Hot Spare | F | DI | DJB-532B |  | 20 Core | 15,16 | X213 | 35,36 | - | - | 5/4 | DI 3. 22 | 27 | I 110.5
165 | LSHH-5180B | Balance TK-506B Level High High | F/ESD | DI | DJB-532A |  | 20 Core | 1,2 | X214 | 1,2 | IR 24-4 | - | 5/4 | DI 3. 23 | 28 | I 110.6
166 | LSH-5180B | Balance TK-506B Level High | F | DI (N.C.) | DJB-532A |  | 20 Core | 3,4 | X214 | 3,4 | - | - | 5/4 | DI 3. 24 | 29 | I 110.7
167 | LSL-5180B | Balance TK-506B Level Low | F | DI (N.C.) | DJB-532B |  | 20 Core | 1,2 | X214 | 5,6 | - | - | 5/4 | DI 3. 25 | 32 | I 111.0
168 | LSLL-5180B | Balance TK-506B Level Low-Low | F | DI (N.C.) | DJB-532B |  | 20 Core | 3,4 | X214 | 7,8 | - | - | 5/4 | DI 3. 26 | 33 | I 111.1
169 | SS-5182A | MOV-5182A Select in Remote | F | DI(N.O.) | DJB-530 | C-2356 | 20 Core | 9,10 | X214 | 13,14 | - | - | 5/4 | DI 3. 27 | 34 | I 111.2
170 | ZSC-5182A | MOV-5182A Closed Position | F | DI(N.O.) | DJB-530 | C-2356 | 20 Core | 13,14 | X214 | 15,16 | - | - | 5/4 | DI 3. 28 | 35 | I 111.3
171 | ZSO-5182A | MOV-5182A Opened Position | F | DI(N.O.) | DJB-530 | C-2356 | 20 Core | 11,12 | X214 | 17,18 | - | - | 5/4 | DI 3. 29 | 36 | I 111.4
172 | PB-ESD1 | Emergency PB Pressed From Site | F/ESD | DI |  |  |  |  | X215 | 3,4 | IR 24-5 | - | 5/4 | DI 3. 30 | 37 | I 111.5
173 | PB-ESD2 | Emergency PB Pressed From Control Panel | ESD | DI |  |  |  |  | - | - | IR 24-1 | - | 5/4 | DI 3. 31 | 38 | I 111.6
174 |  | Hot Spare | F/ESD | DI |  |  |  |  | X215 | 5,6 | IR 24-6 |  | 5/4 | DI 3. 32 | 39 | I 111.7
175 | LSH-5701 | Condensate TK-508 Level High | F | DI (N.C.) |  |  |  |  | X216 | 1,2 | - | - | 5/5 | DI 4. 1 | 2 | I 112.0
176 | LSL-5701 | Condensate TK-508 Level Low | F | DI (N.C.) |  |  |  |  | X216 | 3,4 | - | - | 5/5 | DI 4. 2 | 3 | I 112.1
177 | LSH-5441A | Diesel fuel daily GG-502A Level High | F | DI (N.C.) | DJB-526 | C-5337 |  |  | X216 | 5,6 | - | - | 5/5 | DI 4. 3 | 4 | I 112.2
178 | LSH-5441B | Diesel fuel daily GG-502B Level High | F | DI (N.C.) | DJB-526 | C-5338 |  |  | X216 | 7,8 |  | - | 5/5 | DI 4. 4 | 5 | I 112.3
179 | PSH-5180 | Inlet Crude Oil pressure High | F | DI (N.C.) | DJB-546 | C-53107 | 20 Core | 1,2 | X216 | 9,10 | - | - | 5/5 | DI 4. 5 | 6 | I 112.4
180 | SS-5180 | MOV-5180 Select in Remote | F | DI(N.O.) | DJB-546 | C-53107 | 20 Core | 7,8 | X216 | 11,12 | - | - | 5/5 | DI 4. 6 | 7 | I 112.5
181 | ZSO-5180 | MOV-5180 Opened Position | F | DI(N.O.) | DJB-546 | C-53107 | 20 Core | 9,10 | X216 | 13,14 | - | - | 5/5 | DI 4. 7 | 8 | I 112.6
182 | ZSC-5180 | MOV-5180 Closed Position | F | DI(N.O.) | DJB-546 | C-53107 | 20 Core | 11,12 | X216 | 15,16 | - | - | 5/5 | DI 4. 8 | 9 | I 112.7
183 |  | Hot Spare | F | DI |  |  |  |  | X216 | 17,18 | - | - | 5/5 | DI 4. 9 | 12 | I 113.0
184 | FSL-5510 | Outlet close drain P-508 Flow Low | F | DI (N.C.) | DJB-534 | C-5372 | 20 Core | 1,2 | X217 | 1,2 | - | - | 5/5 | DI 4. 10 | 13 | I 113.1
185 | LSH-5510 | CloseDrain TK-507 Level High | F | DI (N.C.) | DJB-534 | C-5372 | 20 Core | 3,4 | X217 | 3,4 | - | - | 5/5 | DI 4. 11 | 14 | I 113.2
186 | LSL-5510 | CloseDrain TK-507 Level Low | F | DI (N.C.) | DJB-534 | C-5372 | 20 Core | 5,6 | X217 | 5,6 | - | - | 5/5 | DI 4. 12 | 15 | I 113.3
187 | LSHH-5510 | CloseDrain TK-507 Level High High | F | DI (N.C.) | DJB-534 | C-5372 | 20 Core | 7,8 | X217 | 7,8 | - | - | 5/5 | DI 4. 13 | 16 | I 113.4
188 | LSL-5210 | Oily water separator OWS-502 Level Low | F | DI (N.C.) | DJB-534 | C-5372 | 20 Core | 9,10 | X217 | 9,10 | - | - | 5/5 | DI 4. 14 | 17 | I 113.5
189 |  | Hot Spare | F | DI | DJB-534 | C-5372 | 20 Core | 11,12 | X217 | 11,12 | - | - | 5/5 | DI 4. 15 | 18 | I 113.6
190 | FSL-5181A | Discharge of Booster P-511A Flow Low | F | DI (N.C.) | DJB-536 | C-5380 | 20 Core | 1,2 | X218 | 1,2 | - | - | 5/5 | DI 4. 16 | 19 | I 113.7
191 | PSL-5181A | Inlet of Booster P-511A Pressure Low | F | DI (N.C.) | DJB-536 | C-5380 | 20 Core | 3,4 | X218 | 3,4 | - | - | 5/5 | DI 4. 17 | 22 | I 114.0
192 | SS-5185A | MOV-5185A Select in Remote | F | DI(N.O.) | DJB-536 | C-5380 | 20 Core | 9,10 | X218 | 9,10 | - | - | 5/5 | DI 4. 18 | 23 | I 114.1
193 | ZSO-5185A | MOV-5185A Opened Position | F | DI(N.O.) | DJB-536 | C-5380 | 20 Core | 11,12 | X218 | 11,12 | - | - | 5/5 | DI 4. 19 | 24 | I 114.2
194 | ZSC-5185A | MOV-5185A Closed Position | F | DI(N.O.) | DJB-536 | C-5380 | 20 Core | 13,14 | X218 | 13,14 | - | - | 5/5 | DI 4. 20 | 25 | I 114.3
195 |  | Hot Spare | F | DI | DJB-536 | C-5380 | 20 Core | 15,16 | X218 | 15,16 | - | - | 5/5 | DI 4. 21 | 26 | I 114.4
196 | FSL-5181B | Discharge of Booster P-511B Flow Low | F | DI (N.C.) | DJB-538 | C-5384 | 20 Core | 1,2 | X219 | 1,2 | - | - | 5/5 | DI 4. 22 | 27 | I 114.5
197 | PSL-5181B | Inlet of Booster P-511B Pressure Low | F | DI (N.C.) | DJB-538 | C-5384 | 20 Core | 3,4 | X219 | 3,4 | - | - | 5/5 | DI 4. 23 | 28 | I 114.6
198 | SS-5185B | MOV-5185B Select in Remote | F | DI(N.O.) | DJB-538 | C-5384 | 20 Core | 9,10 | X219 | 9,10 | - | - | 5/5 | DI 4. 24 | 29 | I 114.7
199 | ZSO-5185B | MOV-5185B Opened Position | F | DI(N.O.) | DJB-538 | C-5384 | 20 Core | 11,12 | X219 | 11,12 | - | - | 5/5 | DI 4. 25 | 32 | I 115.0
200 | ZSC-5185B | MOV-5185B Closed Position | F | DI(N.O.) | DJB-538 | C-5384 | 20 Core | 13,14 | X219 | 13,14 | - | - | 5/5 | DI 4. 26 | 33 | I 115.1
201 |  | Hot Spare | F/ESD | DI |  |  |  |  | X215 | 7,8 | IR 24-7 | - | 5/5 | DI 4. 27 | 34 | I 115.2
202 | FAN | Fan Fault | F | DI |  |  |  |  | - | - | - | - | 5/5 | DI 4. 28 | 35 | I 115.3
203 | LSH-5440C | Diesel fuel GG-501C Level High | F | DI (N.C.) |  |  |  |  | X21E | 1,2 | - | - | 5/5 | DI 4. 29 | 36 | I 115.4
204 | LSL-5440C | Diesel fuel GG-501C Level Low | F | DI (N.C.) |  |  |  |  | X21E | 3,4 |  |  | 5/5 | DI 4. 30 | 37 | I 115.5
205 | LSH-5441C | Diesel fuel daily GG-502C Level High | F | DI (N.C.) |  |  |  |  | X21E | 5,6 |  |  | 5/5 | DI 4. 31 | 38 | I 115.6
206 |  | Spare | F | DI | [8 empty] | 5/5 | DI 4. 32 | 39 | I 115.7
207 | FSL-5181C | Discharge of Booster P-511C Flow Low | F | DI (N.C.) | DJB-540 | C-5388 | 20 Core | 1,2 | X21A | 1,2 |  |  | 5/6 | DI 5. 1 | 2 | I 116.0
208 | PSL-5181C | Inlet of Booster P-511C Pressure Low | F | DI(N.C.) | DJB-540 | C-5388 | 20 Core | 3,4 | X21A | 3,4 |  |  | 5/6 | DI 5. 2 | 3 | I 116.1
209 | SS-5185C | MOV-5185C Select in Remote | F | DI(N.O.) | DJB-540 | C-5388 | 20 Core | 9,10 | X21A | 9,10 |  |  | 5/6 | DI 5. 3 | 4 | I 116.2
210 | ZSO-5185C | MOV-5185C Opened Position | F | DI(N.O.) | DJB-540 | C-5388 | 20 Core | 11,12 | X21A | 11,12 |  |  | 5/6 | DI 5. 4 | 5 | I 116.3
211 | ZSC-5185C | MOV-5185C Closed Position | F | DI(N.O.) | DJB-540 | C-5388 | 20 Core | 13,14 | X21A | 13,14 |  |  | 5/6 | DI 5. 5 | 6 | I 116.4
212 |  | Hot Spare | F | DI | DJB-540 | C-5388 | 20 Core | 15,16 | X21A | 15,16 |  |  | 5/6 | DI 5. 6 | 7 | I 116.5
213 | FSL-5181D | Discharge of Booster P-511D Flow Low | F | DI (N.C.) | DJB-542 | C-5392 | 20 Core | 1,2 | X21B | 1,2 |  |  | 5/6 | DI 5. 7 | 8 | I 116.6
214 | PSL-5181D | Inlet of Booster P-511D Pressure Low | F | DI(N.C.) | DJB-542 | C-5392 | 20 Core | 3,4 | X21B | 3,4 |  |  | 5/6 | DI 5. 8 | 9 | I 116.7
215 | SS-5185D | MOV-5185D Select in Remote | F | DI(N.O.) | DJB-542 | C-5392 | 20 Core | 9,10 | X21B | 9,10 |  |  | 5/6 | DI 5. 9 | 12 | I 117.0
216 | ZSO-5185D | MOV-5185D Opened Position | F | DI(N.O.) | DJB-542 | C-5392 | 20 Core | 11,12 | X21B | 11,12 |  |  | 5/6 | DI 5. 10 | 13 | I 117.1
217 | ZSC-5185D | MOV-5185D Closed Position | F | DI(N.O.) | DJB-542 | C-5392 | 20 Core | 13,14 | X21B | 13,14 |  |  | 5/6 | DI 5. 11 | 14 | I 117.2
218 |  | Hot Spare | F | DI | DJB-542 | C-5392 | 20 Core | 15,16 | X21B | 15,16 |  |  | 5/6 | DI 5. 12 | 15 | I 117.3
219 | FSL-5181E | Discharge of Booster P-511E Flow Low | F | DI (N.C.) | DJB-544 | C-5396 | 20 Core | 1,2 | X21C | 1,2 |  |  | 5/6 | DI 5. 3 | 16 | I 117.4
220 | PSL-5181E | Inlet of Booster P-511E Pressure Low | F | DI(N.C.) | DJB-544 | C-5396 | 20 Core | 3,4 | X21C | 3,4 |  |  | 5/6 | DI 5. 14 | 17 | I 117.5
221 | SS-5185E | MOV-5185E Select in Remote | F | DI(N.O.) | DJB-544 | C-5396 | 20 Core | 9,10 | X21C | 9,10 |  |  | 5/6 | DI 5. 15 | 18 | I 117.6
222 | ZSO-5185E | MOV-5185E Opened Position | F | DI(N.O.) | DJB-544 | C-5396 | 20 Core | 11,12 | X21C | 11,12 |  |  | 5/6 | DI 5. 16 | 19 | I 117.7
223 | ZSC-5185E | MOV-5185E Closed Position | F | DI(N.O.) | DJB-544 | C-5396 | 20 Core | 13,14 | X21C | 13,14 |  |  | 5/6 | DI 5. 17 | 22 | I 118.0
224 |  | Hot Spare | F | DI | DJB-544 | C-5396 | 20 Core | 15,16 | X21C | 15,16 |  |  | 5/6 | DI 5. 18 | 23 | I 118.1
225 | ZSO-TR503 | TR 503 FEEDER C.B OPEN ALARM | 20KV SWGR | DI |  |  |  |  | X21D | 1,2 |  |  | 5/6 | DI 5. 19 | 24 | I 118.2
226 | XA-TR503 | TR 503 BUCHHOLZ ALARM | 20KV SWGR | DI |  |  |  |  | X21D | 3,4 |  |  | 5/6 | DI 5. 20 | 25 | I 118.3
227 | TSH-TR503 | TR 503 TEMP. ALARM | 20KV SWGR | DI |  |  |  |  | X21D | 5,6 |  |  | 5/6 | DI 5. 21 | 26 | I 118.4
228 | ZSO-TR503 | TR 504 FEEDER C.B OPEN ALARM | 20KV SWGR | DI |  |  |  |  | X21D | 7,8 |  |  | 5/6 | DI 5. 22 | 27 | I 118.5
229 | XA-TR503 | TR 504 BUCHHOLZ ALARM | 20KV SWGR | DI |  |  |  |  | X21D | 9,10 |  |  | 5/6 | DI 5. 23 | 28 | I 118.6
230 | TSH-TR503 | TR 504 TEMP. ALARM | 20KV SWGR | DI |  |  |  |  | X21D | 11,12 |  |  | 5/6 | DI 5. 24 | 29 | I 118.7
231 |  | Hot Spare | 20KV SWGR | DI |  |  |  |  | X21D | 13,14 |  |  | 5/6 | DI 5. 25 | 32 | I 119.0
232 |  | Spare | 20KV SWGR | DI | [8 empty] | 5/6 | DI 5. 26 | 33 | I 119.1
233 |  | Spare | 20KV SWGR | DI | [8 empty] | 5/6 | DI 5. 27 | 34 | I 119.2
234 |  | Spare | 20KV SWGR | DI | [8 empty] | 5/6 | DI 5. 28 | 35 | I 119.3
235 |  | Spare | 20KV SWGR | DI | [8 empty] | 5/6 | DI 5. 29 | 36 | I 119.4
236 |  | Spare | 20KV SWGR | DI | [8 empty] | 5/6 | DI 5. 30 | 37 | I 119.5
237 |  | Spare | 20KV SWGR | DI | [8 empty] | 5/6 | DI 5. 31 | 38 | I 119.6
238 |  | Spare | 20KV SWGR | DI | [8 empty] | 5/6 | DI 5. 32 | 39 | I 119.7
239 | VSH-5181A | Booster P-511A Pump DE Axial Vibration High | F | DI(N.C.) |  |  |  |  | X221 | 1,2 | - | - | 5/7 | DI 6. 1 | 2 | I 120.0
240 | VSH-5182A | Booster P-511A Pump DE Radial Vibration High | F | DI(N.C.) |  |  |  |  | X221 | 3,4 | - | - | 5/7 | DI 6. 2 | 3 | I 120.1
241 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X221 | 5,6 | - | - | 5/7 | DI 6. 3 | 4 | I 120.2
242 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X221 | 7,8 | - | - | 5/7 | DI 6. 4 | 5 | I 120.3
243 | VSHH-5181A | Booster P-511A Pump DE Axial Vibration High High | F | DI(N.C.) |  |  |  |  | X221 | 9,10 | - | - | 5/7 | DI 6. 5 | 6 | I 120.4
244 | VSHH-5182A | Booster P-511A Pump DE Radial Vibration High High | F | DI(N.C.) |  |  |  |  | X221 | 11,12 | - | - | 5/7 | DI 6. 6 | 7 | I 120.5
245 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X221 | 13,14 | - | - | 5/7 | DI 6. 7 | 8 | I 120.6
246 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X221 | 15,16 | - | - | 5/7 | DI 6. 8 | 9 | I 120.7
247 |  | Hot Spare | F | DI |  |  |  |  | X221 | 17,18 | - | - | 5/7 | DI 6. 9 | 12 | I 121.0
248 |  | Hot Spare | F | DI |  |  |  |  | X221 | 19,20 | - | - | 5/7 | DI 6. 10 | 13 | I 121.1
249 | VSH-5181B | Booster P-511B Pump DE Axial Vibration High | F | DI(N.C.) |  |  |  |  | X222 | 1,2 | - | - | 5/7 | DI 6. 11 | 14 | I 121.2
250 | VSH-5182B | Booster P-511B Pump DE Radial Vibration High | F | DI(N.C.) |  |  |  |  | X222 | 3,4 | - | - | 5/7 | DI 6. 12 | 15 | I 121.3
251 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X222 | 5,6 | - | - | 5/7 | DI 6. 13 | 16 | I 121.4
252 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X222 | 7,8 | - | - | 5/7 | DI 6. 14 | 17 | I 121.5
253 | VSHH-5181B | Booster P-511B Pump DE Axial Vibration High High | F | DI(N.C.) |  |  |  |  | X222 | 9,10 | - | - | 5/7 | DI 6. 15 | 18 | I 121.6
254 | VSHH-5182B | Booster P-511B Pump DE Radial Vibration High High | F | DI(N.C.) |  |  |  |  | X222 | 11,12 | - | - | 5/7 | DI 6. 16 | 19 | I 121.7
255 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X222 | 13,14 | - | - | 5/7 | DI 6. 17 | 22 | I 122.0
256 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X222 | 15,16 | - | - | 5/7 | DI 6. 18 | 23 | I 122.1
257 |  | Hot Spare | F | DI |  |  |  |  | X222 | 17,18 | - | - | 5/7 | DI 6. 19 | 24 | I 122.2
258 |  | Hot Spare | F | DI |  |  |  |  | X222 | 19,20 | - | - | 5/7 | DI 6. 20 | 25 | I 122.3
259 | VSH-5181C | Booster P-511C Pump DE Axial Vibration High | F | DI(N.C.) |  |  |  |  | X223 | 1,2 | - | - | 5/7 | DI 6. 21 | 26 | I 122.4
260 | VSH-5182C | Booster P-511C Pump DE Radial Vibration High | F | DI(N.C.) |  |  |  |  | X223 | 3,4 | - | - | 5/7 | DI 6. 22 | 27 | I 122.5
261 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X223 | 5,6 | - | - | 5/7 | DI 6. 23 | 28 | I 122.6
262 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X223 | 7,8 | - | - | 5/7 | DI 6. 24 | 29 | I 122.7
263 | VSHH-5181C | Booster P-511C Pump DE Axial Vibration High High | F | DI(N.C.) |  |  |  |  | X223 | 9,10 | - | - | 5/7 | DI 6. 25 | 32 | I 123.0
264 | VSHH-5182C | Booster P-511C Pump DE Radial Vibration High High | F | DI(N.C.) |  |  |  |  | X223 | 11,12 | - | - | 5/7 | DI 6. 26 | 33 | I 123.1
265 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X223 | 13,14 | - | - | 5/7 | DI 6. 27 | 34 | I 123.2
266 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X223 | 15,16 | - | - | 5/7 | DI 6. 28 | 35 | I 123.3
267 | LSL-5708 | Condensate Tank Low Level | F | DI |  |  |  |  | X223 | 17,18 | - | - | 5/7 | DI 6. 29 | 36 | I 123.4
268 | LSH-5708 | Condensate Tank High Level | F | DI |  |  |  |  | X223 | 19,20 | - | - | 5/7 | DI 6. 30 | 37 | I 123.5
269 |  | Spare | F | DI | [8 empty] | 5/7 | DI 6. 31 | 38 | I 123.6
270 |  | Spare | F | DI | [8 empty] | 5/7 | DI 6. 32 | 39 | I 123.7
271 | VSH-5181D | Booster P-511D Pump DE Axial Vibration High | F | DI(N.C.) |  |  |  |  | X224 | 1,2 | - | - | 5/8 | DI 7.1 | 2 | I 124.0
272 | VSH-5182D | Booster P-511D Pump DE Radial Vibration High | F | DI(N.C.) |  |  |  |  | X224 | 3,4 | - | - | 5/8 | DI 7.2 | 3 | I 124.1
273 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X224 | 5,6 | - | - | 5/8 | DI 7.3 | 4 | I 124.2
274 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X224 | 7,8 | - | - | 5/8 | DI 7.4 | 5 | I 124.3
275 | VSHH-5181D | Booster P-511D Pump DE Axial Vibration High High | F | DI(N.C.) |  |  |  |  | X224 | 9,10 | - | - | 5/8 | DI 7.5 | 6 | I 124.4
276 | VSHH-5182D | Booster P-511D Pump DE Radial Vibration High High | F | DI(N.C.) |  |  |  |  | X224 | 11,12 | - | - | 5/8 | DI 7.6 | 7 | I 124.5
277 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X224 | 13,14 | - | - | 5/8 | DI 7.7 | 8 | I 124.6
278 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X224 | 15,16 | - | - | 5/8 | DI 7.8 | 9 | I 124.7
279 |  | Hot Spare | F | DI |  |  |  |  | X224 | 17,18 | - | - | 5/8 | DI 7.9 | 12 | I 125.0
280 |  | Hot Spare | F | DI |  |  |  |  | X224 | 19,20 | - | - | 5/8 | DI 7.10 | 13 | I 125.1
281 | VSH-5181E | Booster P-511E Pump DE Axial Vibration High | F | DI(N.C.) |  |  |  |  | X225 | 1,2 | - | - | 5/8 | DI 7.11 | 14 | I 125.2
282 | VSH-5182E | Booster P-511E Pump DE Radial Vibration High | F | DI(N.C.) |  |  |  |  | X225 | 3,4 | - | - | 5/8 | DI 7.12 | 15 | I 125.3
283 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X225 | 5,6 | - | - | 5/8 | DI 7.13 | 16 | I 125.4
284 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X225 | 7,8 | - | - | 5/8 | DI 7.14 | 17 | I 125.5
285 | VSHH-5181E | Booster P-511E Pump DE Axial Vibration High High | F | DI(N.C.) |  |  |  |  | X225 | 9,10 | - | - | 5/8 | DI 7.15 | 18 | I 125.6
286 | VSHH-5182E | Booster P-511E Pump DE Radial Vibration High High | F | DI(N.C.) |  |  |  |  | X225 | 11,12 | - | - | 5/8 | DI 7.16 | 19 | I 125.7
287 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X225 | 13,14 | - | - | 5/8 | DI 7.17 | 22 | I 126.0
288 |  | Hot Spare | F | DI(N.C.) |  |  |  |  | X225 | 15,16 | - | - | 5/8 | DI 7.18 | 23 | I 126.1
289 |  | Hot Spare | F | DI |  |  |  |  | X225 | 17,18 | - | - | 5/8 | DI 7.19 | 24 | I 126.2
290 |  | Hot Spare | F | DI |  |  |  |  | X225 | 19,20 | - | - | 5/8 | DI 7.20 | 25 | I 126.3
291 |  | Spare | F | DI | [8 empty] | 5/8 | DI 7.21 | 26 | I 126.4
292 |  | Spare | F | DI | [8 empty] | 5/8 | DI 7.22 | 27 | I 126.5
293 |  | Spare | F | DI | [8 empty] | 5/8 | DI 7.23 | 28 | I 126.6
294 |  | Spare | F | DI | [8 empty] | 5/8 | DI 7.24 | 29 | I 126.7
295 |  | Spare | F | DI | [8 empty] | 5/8 | DI 7.25 | 32 | I 127.0
296 |  | Spare | F | DI | [8 empty] | 5/8 | DI 7.26 | 33 | I 127.1
297 |  | Spare | F | DI | [8 empty] | 5/8 | DI 7.27 | 34 | I 127.2
298 |  | Spare | F | DI | [8 empty] | 5/8 | DI 7.28 | 35 | I 127.3
299 |  | Spare | F | DI | [8 empty] | 5/8 | DI 7.29 | 36 | I 127.4
300 |  | Spare | F | DI | [8 empty] | 5/8 | DI 7.30 | 37 | I 127.5
301 |  | Spare | F | DI | [8 empty] | 5/8 | DI 7.31 | 38 | I 127.6
302 |  | Spare | F | DI | [8 empty] | 5/8 | DI 7.32 | 39 | I 127.7
303 | YI-5510 | Close drain P-508 Running | MCC | DI(N.O.) |  |  |  |  | X231 | 1,2 | - | - | 5/9 | DI 8.1 | 2 | I 128.0
304 | YL-5510 | P-508 Fault | MCC | DI(N.C.) |  |  |  |  | X231 | 3,4 | - | - | 5/9 | DI 8.2 | 3 | I 128.1
305 | SS-5510 | Close drain P-508 Select in Remote | MCC | DI(N.O.) |  |  |  |  | X231 | 5,6 | - | - | 5/9 | DI 8.3 | 4 | I 128.2
306 | YL-5210 | Oil Transfer P-509 Fault | MCC | DI(N.C.) |  |  |  |  | X232 | 1,2 | - | - | 5/9 | DI 8.4 | 5 | I 128.3
307 | YI-5210 | Oil Transfer P-509 Running | MCC | DI(N.O.) |  |  |  |  | X232 | 3,4 | - | - | 5/9 | DI 8.5 | 6 | I 128.4
308 | SS-5210 | Oil Transfer P-509 Select in Remote | MCC | DI(N.O.) |  |  |  |  | X232 | 5,6 | - | - | 5/9 | DI 8.6 | 7 | I 128.5
309 | YL-5440 | Diesel fuel P-504 Fault | MCC | DI(N.C.) |  |  |  |  | X233 | 1,2 | - | - | 5/9 | DI 8.7 | 8 | I 128.6
310 | YI-5440 | Diesel fuel P-504 Running | MCC | DI(N.O.) |  |  |  |  | X233 | 3,4 | - | - | 5/9 | DI 8.8 | 9 | I 128.7
311 | SS-5440 | Diesel fuel P-504 Select in Remote | MCC | DI(N.O.) |  |  |  |  | X233 | 5,6 | - | - | 5/9 | DI 8.9 | 12 | I 129.0
312 | YL-5183A | Mixer M-501A Fault | MCC | DI(N.C.) |  |  |  |  | X234 | 1,2 | - | - | 5/9 | DI 8.10 | 13 | I 129.1
313 | YI-5183A | Mixer M-501A Running | MCC | DI(N.O.) |  |  |  |  | X234 | 3,4 | - | - | 5/9 | DI 8.11 | 14 | I 129.2
314 | SS-5183A | Mixer M-501A Select in Remote | MCC | DI(N.O.) |  |  |  |  | X234 | 5,6 | - | - | 5/9 | DI 8.12 | 15 | I 129.3
315 | YL-5183B | Mixer M-501B Fault | MCC | DI(N.C.) |  |  |  |  | X235 | 1,2 | - | - | 5/9 | DI 8.13 | 16 | I 129.4
316 | YI-5183B | Mixer M-501B Running | MCC | DI(N.O.) |  |  |  |  | X235 | 3,4 | - | - | 5/9 | DI 8.14 | 17 | I 129.5
317 | SS-5183B | Mixer M-501B Select in Remote | MCC | DI(N.O.) |  |  |  |  | X235 | 5,6 | - | - | 5/9 | DI 8.15 | 18 | I 129.6
318 | YL-5183C | Mixer M-501C Fault | MCC | DI(N.C.) |  |  |  |  | X236 | 1,2 | - | - | 5/9 | DI 8.16 | 19 | I 129.7
319 | YI-5183C | Mixer M-501C Running | MCC | DI(N.O.) |  |  |  |  | X236 | 3,4 | - | - | 5/9 | DI 8.17 | 22 | I 130.0
320 | SS-5183C | Mixer M-501C Select in Remote | MCC | DI(N.O.) |  |  |  |  | X236 | 5,6 | - | - | 5/9 | DI 8.18 | 23 | I 130.1
321 | YL-5184A | Mixer M-502A Fault | MCC | DI(N.C.) |  |  |  |  | X237 | 1,2 | - | - | 5/9 | DI 8.19 | 24 | I 130.2
322 | YI-5184A | Mixer M-502A Running | MCC | DI(N.O.) |  |  |  |  | X237 | 3,4 | - | - | 5/9 | DI 8.20 | 25 | I 130.3
323 | SS-5184A | Mixer M-502A Select in Remote | MCC | DI(N.O.) |  |  |  |  | X237 | 5,6 | - | - | 5/9 | DI 8.21 | 26 | I 130.4
324 | YL-5184B | Mixer M-502B Fault | MCC | DI(N.C.) |  |  |  |  | X238 | 1,2 |  |  | 5/9 | DI 8.22 | 27 | I 130.5
325 | YI-5184B | Mixer M-502B Running | MCC | DI(N.O.) |  |  |  |  | X238 | 3,4 |  |  | 5/9 | DI 8.23 | 28 | I 130.6
326 | SS-5184B | Mixer M-502B Select in Remote | MCC | DI(N.O.) |  |  |  |  | X238 | 5,6 |  |  | 5/9 | DI 8.24 | 29 | I 130.7
327 | YL-5184C | Mixer M-502C Fault | MCC | DI(N.C.) |  |  |  |  | X239 | 1,2 |  |  | 5/9 | DI 8.25 | 32 | I 131.0
328 | YI-5184C | Mixer M-502C Running | MCC | DI(N.O.) |  |  |  |  | X239 | 3,4 |  |  | 5/9 | DI 8.26 | 33 | I 131.1
329 | SS-5184C | Mixer M-502C Select in Remote | MCC | DI(N.O.) |  |  |  |  | X239 | 5,6 |  |  | 5/9 | DI 8.27 | 34 | I 131.2
330 | YL-5186A | Booster P-511A Fault | MCC 512 | DI(N.O.) |  |  |  |  | X23A | 1,2 |  |  | 5/9 | DI 8.28 | 35 | I 131.3
331 | YI-5186A | Booster P-511A Running | MCC 512 | DI(N.O.) |  |  |  |  | X23A | 3,4 |  |  | 5/9 | DI 8.29 | 36 | I 131.4
332 | SS-5186A | Booster P-511A Select in Remote | MCC 511 | DI(N.O.) |  |  |  |  | X23A | 5,6 |  |  | 5/9 | DI 8.30 | 37 | I 131.5
333 |  | Hot Spare | MCC 511 | [5 empty] | X23A | 13,14 |  |  | 5/9 | DI 8.31 | 38 | I 131.6
334 |  | Hot Spare | MCC 511 | [5 empty] | X23A | 15,16 |  |  | 5/9 | DI 8.32 | 39 | I 131.7
335 | YL-5186B | Booster P-511B Fault | MCC 511 | DI(N.O.) |  |  |  |  | X23B | 1,2 | - | - | 5/10 | DI 9.1 | 2 | I 132.0
336 | YI-5186B | Booster P-511B Running | MCC 511 | DI(N.O.) |  |  |  |  | X23B | 3,4 | - | - | 5/10 | DI 9.2 | 3 | I 132.1
337 | SS-5186B | Booster P-511B Select in Remote | MCC 511 | DI(N.O.) |  |  |  |  | X23B | 5,6 | - | - | 5/10 | DI 9.3 | 4 | I 132.2
338 | YL-5186C | Booster P-511C Fault | MCC 511 | DI(N.O.) |  |  |  |  | X23C | 1,2 | - | - | 5/10 | DI 9.4 | 5 | I 132.3
339 | YI-5186C | Booster P-511C Running | MCC 512 | DI(N.O.) |  |  |  |  | X23C | 3,4 | - | - | 5/10 | DI 9.5 | 6 | I 132.4
340 | SS-5186C | Booster P-511C Select in Remote | MCC 512 | DI(N.O.) |  |  |  |  | X23C | 5,6 | - | - | 5/10 | DI 9.6 | 7 | I 132.5
341 | YL-5186D | Booster P-511D Fault | MCC 511 | DI(N.O.) |  |  |  |  | X23D | 1,2 | - | - | 5/10 | DI 9.7 | 8 | I 132.6
342 | YI-5186D | Booster P-511D Running | MCC 511 | DI(N.O.) |  |  |  |  | X23D | 3,4 | - | - | 5/10 | DI 9.8 | 9 | I 132.7
343 | SS-5186D | Booster P-511D Select in Remote | MCC 511 | DI(N.O.) |  |  |  |  | X23D | 5,6 | - | - | 5/10 | DI 9.9 | 12 | I 133.0
344 | YL-5186E | Booster P-511E Fault | MCC 511 | DI(N.O.) |  |  |  |  | X23E | 1,2 | - | - | 5/10 | DI 9.10 | 13 | I 133.1
345 | YI-5186E | Booster P-511E Running | MCC 511 | DI(N.O.) |  |  |  |  | X23E | 3,4 | - | - | 5/10 | DI 9.11 | 14 | I 133.2
346 | SS-5186E | Booster P-511E Select in Remote | MCC 512 | DI(N.C.) |  |  |  |  | X23E | 5,6 | - | - | 5/10 | DI 9.12 | 15 | I 133.3
347 | YL-5701A | Condensate P-512A Fault | MCC 512 | DI(N.C.) |  |  |  |  | X23F | 1,2 | - | - | 5/10 | DI 9.13 | 16 | I 133.4
348 | YI-5701A | Condensate P-512A Running | MCC 511 | DI(N.C.) |  |  |  |  | X23F | 3,4 | - | - | 5/10 | DI 9.14 | 17 | I 133.5
349 | SS-5701A | Condensate P-512A Select in Remote | MCC 511 | DI(N.C.) |  |  |  |  | X23F | 5,6 | - | - | 5/10 | DI 9.15 | 18 | I 133.6
350 | YL-5701B | Condensate P-512B Fault | MCC 511 | DI(N.C.) |  |  |  |  | X23G | 1,2 | - | - | 5/10 | DI 9.16 | 19 | I 133.7
351 | YI-5701B | Condensate P-512B Running | MCC 511 | DI(N.C.) |  |  |  |  | X23G | 3,4 | - | - | 5/10 | DI 9.17 | 22 | I 134.0
352 | SS-5701B | Condensate P-512B Select in Remote | MCC 511 | DI(N.C.) |  |  |  |  | X23G | 5,6 | - | - | 5/10 | DI 9.18 | 23 | I 134.1
353 | XA- 511IN1 | MCC 511-IN.1 OVER CURRENT ALARM | MCC 511 | DI |  |  |  |  | X226 | 1,2 | - | - | 5/10 | DI 9.19 | 24 | I 134.2
354 | ZSO-511CBIN1 | MCC 511-IN.1 C.B OPEN ALARM | MCC 511 | DI |  |  |  |  | X226 | 3,4 | - | - | 5/10 | DI 9.20 | 25 | I 134.3
355 | XA- 511IN2 | MCC 511-IN.2 OVER CURRENT ALARM | MCC 511 | DI |  |  |  |  | X226 | 5,6 | - | - | 5/10 | DI 9.21 | 26 | I 134.4
356 | ZSO-511CBIN2 | MCC511-IN.2 C.B OPEN ALARM | MCC 511 | DI |  |  |  |  | X226 | 7,8 | - | - | 5/10 | DI 9.22 | 27 | I 134.5
357 | XA-P511A | P-M-511/ A Booster P-511A General Alarm | MCC 511 | DI |  |  |  |  | X226 | 9,10 | - | - | 5/10 | DI 9.23 | 28 | I 134.6
358 | XA-P511B | P-M-511/ B Booster P-511B General Alarm | MCC 511 | DI |  |  |  |  | X226 | 11,12 | - | - | 5/10 | DI 9.24 | 29 | I 134.7
359 | XA-P511C | P-M-511/ C Booster P-511C General Alarm | MCC 511 | DI |  |  |  |  | X226 | 13,14 | - | - | 5/10 | DI 9.25 | 32 | I 135.0
360 | XA-P511D | P-M-511/ D Booster P-511D General Alarm | MCC 511 | DI |  |  |  |  | X226 | 15,16 | - | - | 5/10 | DI 9.26 | 33 | I 135.1
361 | XA-P511E | P-M-511/ E Booster P-511E General Alarm | MCC 511 | DI |  |  |  |  | X226 | 17,18 | - | - | 5/10 | DI 9.27 | 34 | I 135.2
362 | XA- 512IN1 | MCC 512-IN.1 OVER CURRENT ALARM | MCC 512 | DI |  |  |  |  | X226 | 19,20 | - | - | 5/10 | DI 9.28 | 35 | I 135.3
363 | ZSO-512CBIN1 | MCC 512-IN.1 C.B OPEN ALARM | MCC 512 | DI |  |  |  |  | X226 | 21,22 | - | - | 5/10 | DI 9.29 | 36 | I 135.4
364 | XA- 512IN2 | MCC 512-IN.2 OVER CURRENT ALARM | MCC 512 | DI |  |  |  |  | X226 | 23,24 | - | - | 5/10 | DI 9.30 | 37 | I 135.5
365 | ZSO-512CBIN2 | MCC 512-IN.2 C.B OPEN ALARM | MCC 512 | DI |  |  |  |  | X226 | 25,26 | - | - | 5/10 | DI 9.31 | 38 | I 135.6
366 |  | Hot Spare | MCC 512 | DI |  |  |  |  | X226 | 27,28 | - | - | 5/10 | DI 9.32 | 39 | I 135.7
367 | MOV-5181A-CL | MOV-5181A Close Command | F/ESD | DO (N.C.) | DJB-528 | C-5347 | 20 Core | 7,8 | X213 | 1,2 | IR 11-1 | N.O. | 5/11 | DO 1. 1 | 2 | Q 100.0
368 | MOV-5181A-OP | MOV-5181A Open Command | F | DO (N.O.) | DJB-528 | C-5347 | 20 Core | 9,10 | X213 | 3,4 | IR 11-2 | N.O. | 5/11 | DO 1. 2 | 3 | Q 100.1
369 | MOV-5181B-CL | MOV-5181B Close Command | F/ESD | DO (N.C.) | DJB-532A |  | 20 Core | 5,6 | X213 | 13,14 | IR 11-3 | N.O. | 5/11 | DO 1. 3 | 4 | Q 100.2
370 | MOV-5181B-OP | MOV-5181B Open Command | F | DO (N.O.) | DJB-532A |  | 20 Core | 7,8 | X213 | 15,16 | IR 11-4 | N.O. | 5/11 | DO 1. 4 | 5 | Q 100.3
371 | MOV-5182B-CL | MOV-5182B Close Command | F/ESD | DO (N.C.) | DJB-532B |  | 20 Core | 5,6 | X213 | 25,26 | IR 11-5 | N.O. | 5/11 | DO 1. 5 | 6 | Q 100.4
372 | MOV-5182B-OP | MOV-5182B Open Command | F | DO (N.O.) | DJB-532B |  | 20 Core | 7,8 | X213 | 27,28 | IR 11-6 | N.O. | 5/11 | DO 1. 6 | 7 | Q 100.5
373 | MOV-5182A-CL | MOV-5182A Open Command | F | DO (N.O.) | DJB-530 | C-2356 | 20 Core | 7,8 | X214 | 11,12 | IR 11-7 | N.O. | 5/11 | DO 1. 7 | 8 | Q 100.6
374 | MOV-5182A-OP | MOV-5182A Close Command | F/ESD | DO (N.C.) | DJB-530 | C-2356 | 20 Core | 5,6 | X214 | 9,10 | IR 11-8 | N.O. | 5/11 | DO 1. 8 | 9 | Q 100.7
375 | MOV-5185A-CL | MOV-5185A Close Command | F | DO (N.O.) | DJB-536 | C-5380 | 20 Core | 5,6 | X218 | 5,6 | IR 11-9 | N.O. | 5/11 | DO 1. 9 | 12 | Q 101.0
376 | MOV-5185A-OP | MOV-5185A Open Command | F | DO (N.O.) | DJB-536 | C-5380 | 20 Core | 7,8 | X218 | 7,8 | IR 11-10 | N.O. | 5/11 | DO 1. 10 | 13 | Q 101.1
377 | MOV-5185B-CL | MOV-5185B Close Command | F | DO (N.O.) | DJB-538 | C-5384 | 20 Core | 5,6 | X219 | 5,6 | IR 11-11 | N.O. | 5/11 | DO 1. 11 | 14 | Q 101.2
378 | MOV-5185B-OP | MOV-5185B Open Command | F | DO (N.O.) | DJB-538 | C-5384 | 20 Core | 7,8 | X219 | 7,8 | IR 11-12 | N.O. | 5/11 | DO 1. 12 | 15 | Q 101.3
379 | MOV-5185C-CL | MOV-5185C Close Command | F | DO (N.O.) | DJB-540 | C-5388 | 20 Core | 5,6 | X21A | 5,6 | IR 11-13 | N.O. | 5/11 | DO 1. 13 | 16 | Q 101.4
380 | MOV-5185C-OP | MOV-5185C Open Command | F | DO (N.O.) | DJB-540 | C-5388 | 20 Core | 7,8 | X21A | 7,8 | IR 11-14 | N.O. | 5/11 | DO 1. 14 | 17 | Q 101.5
381 | MOV-5185D-CL | MOV-5185D Close Command | F | DO (N.O.) | DJB-542 | C-5392 | 20 Core | 5,6 | X21B | 5,6 | IR 11-15 | N.O. | 5/11 | DO 1 .15 | 18 | Q 101.6
382 | MOV-5185D-OP | MOV-5185D Open Command | F | DO (N.O.) | DJB-542 | C-5392 | 20 Core | 7,8 | X21B | 7,8 | IR 11-16 | N.O. | 5/11 | DO 1. 16 | 19 | Q 101.7
383 | MOV-5185E-CL | MOV-5185E Close Command | F | DO (N.O.) | DJB-544 | C-5396 | 20 Core | 5,6 | X21C | 5,6 | IR 11-17 | N.O. | 5/11 | DO 1. 17 | 22 | Q 102.0
384 | MOV-5185E-OP | MOV-5185E Open Command | F | DO (N.O.) | DJB-544 | C-5396 | 20 Core | 7,8 | X21C | 7,8 | IR 11-18 | N.O. | 5/11 | DO 1. 18 | 23 | Q 102.1
385 | MOV-5180-OP | MOV-5180 Open Command | F | DO (N.O.) | DJB-546 | C-53107 | 20 Core | 5,6 | X216 | 19,20 | IR 11-19 | N.O. | 5/11 | DO 1. 19 | 24 | Q 102.2
386 | MOV-5180-CL | MOV-5180 Close Command | F/ESD | DO (N.C.) | DJB-546 | C-53107 | 20 Core | 3,4 | X216 | 21,22 | IR 11-20 | N.O. | 5/11 | DO 1. 20 | 25 | Q 102.3
387 |  | Hot Spare | F | DO |  |  |  |  | X216 | 23,24 | IR 11-21 | N.O. | 5/11 | DO 1. 21 | 26 | Q 102.4
388 |  | Hot Spare | F | DO |  |  |  |  | X216 | 25,26 | IR 11-22 | N.O. | 5/11 | DO 1. 22 | 27 | Q 102.5
389 |  | Hot Spare | F/ESD | DO |  |  |  |  | X216 | 27,28 | IR 11-23 | N.O. | 5/11 | DO 1. 23 | 28 | Q 102.6
390 |  | Hot Spare | F/ESD | DO |  |  |  |  | X216 | 29,30 | IR 11-24 | N.O. | 5/11 | DO 1. 24 | 29 | Q 102.7
391 |  | Spare | F | DO | [7 empty] | N.O. | 5/11 | DO 1. 25 | 32 | Q 103.0
392 |  | Spare | F | DO | [7 empty] | N.O. | 5/11 | DO 1. 26 | 33 | Q 103.1
393 |  | Spare | F | DO | [7 empty] | N.O. | 5/11 | DO 1. 27 | 34 | Q 103.2
394 |  | Spare | F | DO | [8 empty] | 5/11 | DO 1. 28 | 35 | Q 103.3
395 |  | Spare | F | DO | [8 empty] | 5/11 | DO 1. 29 | 36 | Q 103.4
396 |  | Spare | F | DO | [8 empty] | 5/11 | DO 1. 30 | 37 | Q 103.5
397 |  | Spare | F | DO | [8 empty] | 5/11 | DO 1. 31 | 38 | Q 103.6
398 |  | Spare | F | DO | [8 empty] | 5/11 | DO 1. 32 | 39 | Q 103.7
399 | P-511A-ST | Booster P-511A Start Command | MCC 511 | DO(N.O.) |  |  |  |  | X23A | 7,8 | IR 12-1 | N.O. | 5/12 | DO 2. 1 | 2 | Q 104.0
400 | P-511A-SP | Booster P-511A Stop Command | MCC 511 | DO(N.C.) |  |  |  |  | X23A | 9,10 | IR 12-2 | N.O. | 5/12 | DO 2. 2 | 3 | Q 104.1
401 | P-511A-ST-PER | Booster P-511A Start Permission | MCC 511 | DO(N.C.) |  |  |  |  | X23A | 11,12 | IR 12-3 | N.O. | 5/12 | DO 2. 3 | 4 | Q 104.2
402 | P-511B-ST | Booster P-511B Start Command | MCC 511 | DO(N.O.) |  |  |  |  | X23B | 7,8 | IR 12-4 | N.O. | 5/12 | DO 2. 4 | 5 | Q 104.3
403 | P-511B-SP | Booster P-511B Stop Command | MCC 511 | DO(N.C.) |  |  |  |  | X23B | 9,10 | IR 12-5 | N.O. | 5/12 | DO 2. 5 | 6 | Q 104.4
404 | P-511B-ST-PER | Booster P-511B Start Permission | MCC 511 | DO(N.C.) |  |  |  |  | X23B | 11,12 | IR 12-6 | N.O. | 5/12 | DO 2. 6 | 7 | Q 104.5
405 | P-511C-ST | Booster P-511C Start Command | MCC 511 | DO(N.O.) |  |  |  |  | X23C | 7,8 | IR 12-7 | N.O. | 5/12 | DO 2. 7 | 8 | Q 104.6
406 | P-511C-SP | Booster P-511C Stop Command | MCC 511 | DO(N.C.) |  |  |  |  | X23C | 9,10 | IR 12-8 | N.O. | 5/12 | DO 2. 8 | 9 | Q 104.7
407 | P-511C-ST-PER | Booster P-511C Start Permission | MCC 511 | DO(N.C.) |  |  |  |  | X23C | 11,12 | IR 12-9 | N.O. | 5/12 | DO 2. 9 | 12 | Q 105.0
408 | P-511D-ST | Booster P-511D Start Command | MCC 511 | DO(N.O.) |  |  |  |  | X23D | 7,8 | IR 12-10 | N.O. | 5/12 | DO 2. 10 | 13 | Q 105.1
409 | P-511D-SP | Booster P-511D Stop Command | MCC 511 | DO(N.C.) |  |  |  |  | X23D | 9,10 | IR 12-11 | N.O. | 5/12 | DO 2. 11 | 14 | Q 105.2
410 | P-511D-ST-PER | Booster P-511D Start Permission | MCC 511 | DO(N.C.) |  |  |  |  | X23D | 11,12 | IR 12-12 | N.O. | 5/12 | DO 2 .12 | 15 | Q 105.3
411 | P-511E-ST | Booster P-511E Start Command | MCC 511 | DO(N.O.) |  |  |  |  | X23E | 7,8 | IR 12-13 | N.O. | 5/12 | DO 2. 13 | 16 | Q 105.4
412 | P-511E-SP | Booster P-511E Stop Command | MCC 511 | DO(N.C.) |  |  |  |  | X23E | 9,10 | IR 12-14 | N.O. | 5/12 | DO 2 .14 | 17 | Q 105.5
413 | P-511E-ST-PER | Booster P-511E Start Permission | MCC 511 | DO(N.C.) |  |  |  |  | X23E | 11,12 | IR 12-15 | N.O. | 5/12 | DO 2. 15 | 18 | Q 105.6
414 | P-512A-ST | Condensate P-512A Start Command | MCC 512 | DO(N.O.) |  |  |  |  | X23F | 7,8 | IR 12-16 | N.O. | 5/12 | DO 2. 16 | 19 | Q 105.7
415 | P-512A-SP | Condensate P-512A Stop Command | MCC 512 | DO(N.C.) |  |  |  |  | X23F | 9,10 | IR 12-17 | N.O. | 5/12 | DO 2. 17 | 22 | Q 106.0
416 | P-512A-ST-PER | Condensate P-512A Start Permission | MCC 512 | DO(N.C.) |  |  |  |  | X23F | 11,12 | IR 12-18 | N.O. | 5/12 | DO 2. 18 | 23 | Q 106.1
417 | P-512B-ST | Condensate P-512B Start Command | MCC 512 | DO(N.O.) |  |  |  |  | X23G | 7,8 | IR 12-19 | N.O. | 5/12 | DO 2. 19 | 24 | Q 106.2
418 | P-512B-SP | Condensate P-512B Stop Command | MCC 512 | DO (N.O.) |  |  |  |  | X23G | 9,10 | IR 12-20 | N.O. | 5/12 | DO 2. 20 | 25 | Q 106.3
419 | P-512B-ST-PER | Condensate P-512B Start Permission | MCC 512 | DO(N.C.) |  |  |  |  | X23G | 11,12 | IR 12-21 | N.O. | 5/12 | DO 2. 21 | 26 | Q 106.4
420 |  | Reset to Vibration | MCC 511 | DO (N.C.) |  |  |  |  | X23G | 13,14 | IR 12-22 | N.O. | 5/12 | DO 2. 22 | 27 | Q 106.5
421 |  | Reset to Vibration | MCC 512 | DO (N.C.) |  |  |  |  | X23G | 15,16 | IR 12-23 | N.O. | 5/12 | DO 2. 23 | 28 | Q 106.6
422 |  | Spare | MCC 511 | DO | [8 empty] | 5/12 | DO 2. 24 | 29 | Q 106.7
423 |  | Spare | MCC 511 | DO | [8 empty] | 5/12 | DO 2. 25 | 32 | Q 107.0
424 |  | Spare | MCC 511 | DO | [8 empty] | 5/12 | DO 2. 26 | 33 | Q 107.1
425 |  | Spare | MCC 511 | DO | [8 empty] | 5/12 | DO 2. 27 | 34 | Q 107.2
426 |  | Spare | MCC 511 | DO | [8 empty] | 5/12 | DO 2. 28 | 35 | Q 107.3
427 |  | Spare | MCC 512 | DO | [8 empty] | 5/12 | DO 2. 29 | 36 | Q 107.4
428 |  | Spare | MCC 512 | DO | [8 empty] | 5/12 | DO 2. 30 | 37 | Q 107.5
429 |  | Spare | MCC 512 | DO | [8 empty] | 5/12 | DO 2. 31 | 38 | Q 107.6
430 |  | Spare | MCC 512 | DO | [8 empty] | 5/12 | DO 2. 32 | 39 | Q 107.7
431 | P-508-ST-PER | Close drain P-508 Start Permission | MCC | DO(N.O.) |  |  |  |  | X231 | 7,8 | IR 13-1 | N.O. | 5/13 | DO 3.1 | 2 | Q 108.0
432 | P-508-ST | Close drain P-508 Start Command | MCC | DO(N.C.) |  |  |  |  | X231 | 9,10 | IR 13-2 | N.O. | 5/13 | DO 3.2 | 3 | Q 108.1
433 | P-508-SP | Close drain P-508 Stop Command | MCC | DO(N.C.) |  |  |  |  | X231 | 11,12 | IR 13-3 | N.O. | 5/13 | DO 3.3 | 4 | Q 108.2
434 | P-504-ST-PER | Diesel fuel P-504 Start Permission | MCC | DO(N.C.) |  |  |  |  | X233 | 7,8 | IR 13-4 | N.O. | 5/13 | DO 3.4 | 5 | Q 108.3
435 | P-504-ST | Diesel fuel P-504 Start Command | MCC | DO(N.O.) |  |  |  |  | X233 | 9,10 | IR 13-5 | N.O. | 5/13 | DO 3.5 | 6 | Q 108.4
436 | P-504-SP | Diesel fuel P-504 Stop Command | MCC | DO(N.C.) |  |  |  |  | X233 | 11,12 | IR 13-6 | N.O. | 5/13 | DO 3.6 | 7 | Q 108.5
437 | M-501A-ST-PER | MIXER M-501A Start Permission | MCC | DO(N.O.) |  |  |  |  | X234 | 7,8 | IR 13-7 | N.O. | 5/13 | DO 3.7 | 8 | Q 108.6
438 | M-501A-ST | MIXER M-501A Start Command | MCC | DO(N.C.) |  |  |  |  | X234 | 9,10 | IR 13-8 | N.O. | 5/13 | DO 3.8 | 9 | Q 108.7
439 | M-501A-SP | MIXER M-501A Stop Command | MCC | DO(N.C.) |  |  |  |  | X234 | 11,12 | IR 13-9 | N.O. | 5/13 | DO 3.9 | 12 | Q 109.0
440 | M-501B-ST-PER | MIXER M-501B Start Permission | MCC | DO(N.O.) |  |  |  |  | X235 | 7,8 | IR 13-10 | N.O. | 5/13 | DO 3.10 | 13 | Q 109.1
441 | M-501B-ST | MIXER M-501B Start Command | MCC | DO(N.C.) |  |  |  |  | X235 | 9,10 | IR 13-11 | N.O. | 5/13 | DO 3.11 | 14 | Q 109.2
442 | M-501B-SP | MIXER M-501B Stop Command | MCC | DO(N.C.) |  |  |  |  | X235 | 11,12 | IR 13-12 | N.O. | 5/13 | DO 3.12 | 15 | Q 109.3
443 | M-501C-ST-PER | MIXER M-501C Start Permission | MCC | DO(N.O.) |  |  |  |  | X236 | 7,8 | IR 13-13 | N.O. | 5/13 | DO 3.13 | 16 | Q 109.4
444 | M-501C-ST | MIXER M-501C Start Command | MCC | DO(N.C.) |  |  |  |  | X236 | 9,10 | IR 13-14 | N.O. | 5/13 | DO 3.14 | 17 | Q 109.5
445 | M-501C-SP | MIXER M-501C Stop Command | MCC | DO(N.C.) |  |  |  |  | X236 | 11,12 | IR 13-15 | N.O. | 5/13 | DO 3.15 | 18 | Q 109.6
446 | M-502A-ST-PER | MIXER M-502A Start Permission | MCC | DO(N.O.) |  |  |  |  | X237 | 7,8 | IR 13-16 | N.O. | 5/13 | DO 3.16 | 19 | Q 109.7
447 | M-502A-ST | MIXER M-502A Start Command | MCC | DO(N.C.) |  |  |  |  | X237 | 9,10 | IR 13-17 | N.O. | 5/13 | DO 3.17 | 22 | Q 110.0
448 | M-502A-SP | MIXER M-502A Stop Command | MCC | DO(N.C.) |  |  |  |  | X237 | 11,12 | IR 13-18 | N.O. | 5/13 | DO 3.18 | 23 | Q 110.1
449 | M-502B-ST-PER | MIXER M-502B Start Permission | MCC | DO(N.O.) |  |  |  |  | X238 | 7,8 | IR 13-19 | N.O. | 5/13 | DO 3.19 | 24 | Q 110.2
450 | M-502B-ST | MIXER M-502B Start Command | MCC | DO(N.C.) |  |  |  |  | X238 | 9,10 | IR 13-20 | N.O. | 5/13 | DO 3.20 | 25 | Q 110.3
451 | M-502B-SP | MIXER M-502B Stop Command | MCC | DO(N.C.) |  |  |  |  | X238 | 11,12 | IR 13-21 | N.O. | 5/13 | DO 3.21 | 26 | Q 110.4
452 | M-502C-ST-PER | MIXER M-502C Start Permission | MCC | DO(N.O.) |  |  |  |  | X239 | 7,8 | IR 13-22 | N.O. | 5/13 | DO 3.22 | 27 | Q 110.5
453 | M-502C-ST | MIXER M-502C Start Command | MCC | DO(N.C.) |  |  |  |  | X239 | 9,10 | IR 13-23 | N.O. | 5/13 | DO 3.23 | 28 | Q 110.6
454 | M-502C-SP | MIXER M-502C Stop Command | MCC | DO(N.C.) |  |  |  |  | X239 | 11,12 | IR 13-24 | N.O. | 5/13 | DO 3.24 | 29 | Q 110.7
455 | P-509-ST-PER | Oil Transfer P-509 Start Permissiond | MCC | DO(N.O.) |  |  |  |  | X232 | 7,8 | IR 13-25 | N.O. | 5/13 | DO 3.25 | 32 | Q 111.0
456 | P-509-ST | Oil Transfer P-509 Start Command | MCC | DO(N.C.) |  |  |  |  | X232 | 9,10 | IR 13-26 | N.O. | 5/13 | DO 3.26 | 33 | Q 111.1
457 | P-509-SP | Oil Transfer P-509 Stop Command | MCC | DO(N.C.) |  |  |  |  | X232 | 11,12 | IR 13-27 | N.O. | 5/13 | DO 3.27 | 34 | Q 111.2
458 |  | Hot Spare | MCC | DO |  |  |  |  | X232 | 13,14 | IR 13-28 | N.O. | 5/13 | DO 3.28 | 35 | Q 111.3
459 |  | Hot Spare | MCC | DO |  |  |  |  | X232 | 15,16 | IR 13-29 | N.O. | 5/13 | DO 3.29 | 36 | Q 111.4
460 |  | Spare | MCC | DO | [8 empty] | 5/13 | DO 3.30 | 37 | Q 111.5
461 |  | Spare | MCC | DO | [8 empty] | 5/13 | DO 3.31 | 38 | Q 111.6
462 |  | Spare | MCC | DO | [8 empty] | 5/13 | DO 3.32 | 39 | Q 111.7
Note on A147: ws021:
Note on A300: ws021: