## Cover Page
|  | Moghanak Pump Station Balance Tanks Fat Punch List Material Take Off |  | National Iranian Oil Engineering and Construction Company (NIOEC)
Control Sazan pooyande Co. |  | Iran Caspian Oil Transfer & Refining Project Sari Pump Station & Moghanak Terminal Balance Tanks Project |  | Page : 1 of 4 |  | Rev: B
Moghanak Pump Station Balance Tanks Fat Punch List Material Take Off
B | FAT Punch List |  | Z.P | S.Shojaei | H.Khodam | 2014-03-10
A | Preliminary |  | Z.P | S.Shojaei | H.Khodam | 2012-07-15
Rev. | Description |  | Design | Check | Approv. | Date

## MTO
|  |  | Moghanak Pump Station Balance Tanks Material Take off | [5 empty] | National Iranian Oil Engineering and Construction Company (NIOEC)
Control Sazan pooyande Co. |  |  | Iran Caspian Oil Transfer & Refining Project Sari Pump Station & Moghanak Terminal Balance Tanks Project | [5 empty] | Page : of 4 | [8 empty] | B
ITEM | CODE | DESCRIPTION |  | MODEL | MANUFACTURE |  | ORDER NOMBER |  |  |  | UNIT | QUANTITY PER CABINET |  |  | VISUAL INSPECTION |  |  | REMARK
[12 empty] | CP |  | TOTQL | CP |  | TOTQL
[12 empty] | #1 | #2 |  | #1 | #2
1 | Rail | Rail for ET 200M, 530mm long |  |  | SIEMENS |  | 6ES7 | 195- | 1GF30 | -0XA0 | pcs | 2 | 1 | 3
2 | IM | Profibus interface for ET 200M and CPU |  |  | SIEMENS |  | 6ES7 | 153- | 2AR03 | -0XA0 | pack | 2 | 1 | 3
3 | BUS COUPLER | DP Bus connector without PG socket |  |  | SIEMENS |  | 6ES7 | 972- | 0BA51 | -0XA0 | pcs | 3 | 3 | 6
4 | BM_IO | Bus module for I/O cards insert/remove capability | F |  | SIEMENS | 1,2,Sh | 6ES7 | 195- | 7BH00 | -0XA0 | pcs | 8 | 7 | 15
5 | DI | Digital input card, 32 ch |  |  | SIEMENS | 1,2,Sh | 6ES7 | 321- | 1BL00 | 0AA0 | pcs | 5 | 4 | 9
6 | DO | Digital output card, 32 ch |  |  | SIEMENS |  | 6ES7 | 322- | 1BL00 | 0AA0 | pcs | 2 | 1 | 3
7 | AI | Anolog input card, 8 ch |  |  | SIEMENS | 3,4,Sh | 6ES7 | 331- | 7KF02 | 0AB0 | pcs | 8 | 3 | 11
8 | FC | Front Connector for DI, Do, AI & AO cards |  |  | SIEMENS |  | 6ES7 | 3922- | 1AJ00 | 0AA0 | pcs | 16 | 10 | 26
9 | AI_BR | Anolog input Barrier |  | D1010D | GMI |  | D1010D |  |  |  | pcs | 9 | 0 | 9
10 | RTD_BR | RTD Barrier |  | D1072D | GMI |  | D1072D |  |  |  | pcs | 20 | 0 | 20
11 | RL1 | Interposing Relay, 24VDC, SPDT 1CO/6A. |  | 29 6617 / 011 / 6 | Phonix Contact |  | 29 6617 | /011 | /6 |  | pcs | 83 | 0 | 83
12 | RL2 | Interposing Relay, 24VDC,DPDT 2CO/6A. |  | 29 6706 / 010 / 5 | Phonix Contact |  | 29 6706 | /010 | /5 |  | pcs | 0 | 28 | 28
13 | TIMER | Timer Solid state, 1SPDT |  | H3DE-M1 | OMRON | [5 empty] | pcs | 2 | 0 | 2
14 | SOCKET | 220VAC Power socket |  | 220VAC | Phoenix Contact |  | 29 64 499 |  |  |  | pcs | 0 | 1 | 1
15 | TRM_1 | Terminal block, for wire up to 4mm² |  | RTP2.5 | RAAD | [5 empty] | pcs | 300 | 293 | 593
16 | TRM_2 | Terminal block blue, for wire up to 4mm² |  | RTP2.5-Blue | RAAD | [5 empty] | pcs | 38 | 36 | 74
17 | TRM_2 | Terminal block, for wire up to 4mm² |  | RTP2.5 | RAAD | [5 empty] | pcs | 10 | 4 | 14
18 | TRM_3 | Test disconnect terminal, for wire up to 4mm² |  | RDT2.5-C | RAAD |  | - |  |  |  | pcs | 20 | 4 | 24
19 | TRM_4 | Test disconnect terminal Blue, for wire up to 4mm² |  | RDT2.5-C-Blue | RAAD |  | - |  |  |  | pcs | 100 | 74 | 174
20 | TRM_5 | Fused terminal, with LED, for wire up to 4mm², 24 VDC |  | RFT5-LD | RAAD |  | - |  |  |  | pcs | 200 | 86 | 286
21 | FUSE | Fast fuse (1A), Length: 20mm |  | 1A (5×20 mm) | - |  | - |  |  |  | pcs | 200 | 86 | 286
22 | LABEL | Terminal strip label (Marker carrier) |  | LB/2 | RAAD |  | - |  |  |  | pcs | 72 | 26 | 98
23 | LOCK | End clamp for supporting terminals (End bracket) |  | EB/1 & EB/2 | RAAD |  | - |  |  |  | pcs | 13 | 10 | 23
24 | MCB 2S | Miniature fuse single pole |  | 2A (S) | Sherak |  | FAZ-C2 |  |  |  | pcs | 1 | 1 | 2
25 | MCB 6S | Miniature fuse single pole |  | 6A (S) | Sherak |  | FAZ-C6 |  |  |  | pcs | 1 | 0 | 1
26 | MCB 2D | Miniature fuse double pole |  | 2A (D) | Sherak |  | FAZ-C2/2 |  |  |  | pcs | 1 | 0 | 1
27 | MCB 10D | Miniature fuse double pole |  | 10A (D) | Sherak |  | FAZ-C10/2 |  |  |  | pcs | 1 | 1 | 2
28 | MCB_AUX | Auxilary contact for Miniature fuse |  |  | Sherak | [5 empty] | pcs | 1 | 1 | 2
29 | EMG PB | Emergancy push button door |  | Telemecanique |  |  | - |  |  |  | pcs | 1 | 0 | 1
30 | PB | Push button 24VDC |  | Telemecanique | Red/Green/Yellow |  | - |  |  |  | pcs | 3 | 0 | 3
31 | SL | Signal lamp 24VDC/Red |  | Telemecanique |  |  | - |  |  |  | pcs | 9 | 0 | 9
32 | Horn | HOCHIKI Multi-tone electronic siren, 24VDC |  | Banshee | Hosiden besson |  | - |  |  |  | pcs | 1 | 0 | 1
33 | FAN | Cabinet ventilation fan (24 VDC) with filter |  | 25 x 25 Cm | Rittal Type |  | SK 33 25.024 |  |  |  | pcs | 1 | 0 | 1
34 | FILTER | Cabinet filter |  | 25 x 25 Cm | Rittal Type |  | SK 33 25.207 |  |  |  | pcs | 1 | 1 | 2
35 | THER | Cabinet thermostat |  | Thermostat | Rittal |  | - |  |  |  | pcs | 1 | 0 | 1
36 | TSH | Temperature switch, set 45°C |  | 45°C | Local |  | - |  |  |  | pcs | 1 | 0 | 1
37 | HEAT | Heater for control panel |  | Heater (100W) | Local |  | - |  |  |  | pcs | 1 | 0 | 1
38 | DLS | Door limit switch |  | - | Local |  | - |  |  |  | pcs | 2 | 2 | 4
39 | LIGHT | Florescent lighting |  | 18W | Mazi noor |  | - |  |  |  | pcs | 2 | 2 | 4
40 | DOOR-S | Cabinet door stay |  | Door Stay | Local |  | - |  |  |  | pcs | 2 | 2 | 4
41 | MAP_HOLD. | Document holder |  | Map Holder | Local |  | - |  |  |  | pcs | 1 | 1 | 2
42 | PE_BAR | Protective earth bus bar |  | PE Bar | Local |  | - |  |  |  | pcs | 1 | 0 | 1
43 | IE_BAR | Instrument earth bus bar |  | IE Bar | Local |  | - |  |  |  | pcs | 1 | 1 | 2
44 | ISE_BAR | Intrinsically safe earth bus bar |  | ISE Bar | Local |  | - |  |  |  | pcs | 0 | 1 | 1
45 | DIN-RAIL | 35 mm Rail |  | - | Local |  | - |  |  |  | m
46 | WIRE | Interconnection wires |  |  | Zarsim |  | - |  |  |  | m