## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 27
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0016 | D04
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT نگهداشت و افزایش تولید میدان نفتی بینک
D04 |  | NOV.2024 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Sadeghian
D03 |  | AUG.2024 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Sadeghian
D02 |  | FEB.2024 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D01 |  | OCT.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | MAY.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: 'F9Z-708936
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 27
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0016 |  | D04
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  | X |  | 65
2 | X | X | X |  | X |  | X |  | 66
3 | X | X |  |  |  |  | X |  | 67
4 | X | [5 empty] | X |  | 68
5 | X | X | X |  |  |  | X |  | 69
6 | X | X | X |  |  |  | X |  | 70
7 | X | X | X |  | X |  | X |  | 71
8 | X | X | X |  | X |  | X |  | 72
9 | X | X | X |  | X |  | X |  | 73
10 | X | X | X |  | X |  | X |  | 74
11 | X | X | X |  | X |  | X |  | 75
12 | X | X | X |  | X |  | X |  | 76
13 | X | X | X |  |  |  | X |  | 77
14 | X | X | X |  | X |  | X |  | 78
15 | X | X | X |  | X |  |  |  | 79
16 | X |  | X |  | X |  | X |  | 80
17 | X | X | X |  | X |  |  |  | 81
18 | X |  | X |  | X |  | X |  | 82
19 | X | X | X |  | X |  |  |  | 83
20 | X |  | X |  | X |  | X |  | 84
21 | X | X | X |  |  |  | X |  | 85
22 | X | X | X |  | X |  | X |  | 86
23 | X | X | X | [5 empty] | 87
24 | X | X | X |  | X |  | X |  | 88
25 | X | X | X | [5 empty] | 89
26 |  | X | X |  | X |  | X |  | 90
27 |  | X | X |  | X |  |  |  | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Reference
NISOC | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 27
9184 – 073 - 053 | BK | GCS | PEDCO | 120 | IN | DT | 0016 | D04
REFERENECE DOCUMENT
F&G Location Layout For Process AREA | [6 empty] | BK-GCS-PEDCO-120-IN-PY-0005
F&G Location Layout For Buildings | [6 empty] | BK-GCS-PEDCO-120-IN-PY-0006
FIRE & GAS DETECTION DESIGN CRITERIA | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0001
SPEC. FOR FIRE & GAS SENSOR AND DEVICES | [6 empty] | BK-00-HD-000-IN-SP-0009-D00
F&G Cause and Effect Diagram For Process Area | [6 empty] | BK-GCS-PEDCO-120-IN-DG-0009
F&G Cause and Effect Diagram For Buildings | [6 empty] | BK-GCS-PEDCO-120-IN-DG-0010

## Note 1
NISOC | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4از 27
9184 – 073 - 053 | BK | GCS | PEDCO | 120 | IN | DT | 0016 | D04
GENERAL NOTES:
1 - Vendor shall identify and detail any deviation from the present Data Sheet
2- All equipments/detectors listed in this document shall be supplied with related calibration and test equipments.
3 - S.S. Name plate including project description to be provided.
4- Low power consumption to be considered.

## CONTENTS
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 27
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | IN | DT | 0016 | D04
CONTENTS
| ITEMS | [9 empty] | PAGES
| DATASHEET FOR FLAMMABLE GAS DETECTOR |  |  |  | ………………………………………………………………………….. | [5 empty] | 6
| FLAMMABLE GAS DETECTOR LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 7
| DATASHEET FOR TOXIC GAS DETECTOR |  |  |  | ………………………………………………………………………….. | [5 empty] | 8
| TOXIC GAS DETECTOR LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 9
| DATASHEET FOR FLAME DETECTOR |  |  |  | ………………………………………………………………………….. | [5 empty] | 10
| FLAME DETECTOR LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 11
| DATASHEET FOR HORN |  |  |  | ………………………………………………………………………….. | [5 empty] | 12
| HORN DETECTOR LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 13
| DATASHEET FOR BEACON |  |  |  | ………………………………………………………………………….. | [5 empty] | 14
| BEACON LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 15
| DATASHEET FOR HYDROGEN GAS DETECTOR |  |  |  | ………………………………………………………………………….. | [5 empty] | 16
| HYDROGEN GAS DETECTOR LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 17
| DATASHEET FOR MANUAL ALARM CALL POINT |  |  |  | ………………………………………………………………………….. | [5 empty] | 18
| MANUAL ALARM CALL POINT LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 19
| DATASHEET FOR LINEAR HEAT DETECTOR |  |  |  | ………………………………………………………………………….. | [5 empty] | 20
| LINEAR HEAT DETECTOR LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 21
| DATASHEET FOR SMOKE DETECTOR |  |  |  | ………………………………………………………………………….. | [5 empty] | 22
| SMOKE DETECTOR LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 23
| DATASHEET FOR BELL |  |  |  | ………………………………………………………………………….. | [5 empty] | 24
| BELL LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 25
| DATASHEET FOR HEAT DETECTOR |  |  |  | ………………………………………………………………………….. | [5 empty] | 26
| HEAT DETECTOR LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 27

## FGD
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 6 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN |  | DT | 0016 | D04
DATASHEET FOR FLAMMABLE GAS DETECTOR
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic, Harsh and Dusty
| 5 | Area Classification | [5 empty] | See Next Page'
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | Function | [5 empty] | Flammable Gas Detector (HC)
| 9 | Service | [5 empty] | See Next Page
| 9 | Case Color | [5 empty] | Red
| 10 | Detector Type | [5 empty] | Conventional
| 11 | Sensor Type | [5 empty] | Infra Red (IR)
| 12 | Covering Range | [5 empty] | 75 m2
| 13 | Accuracy | [5 empty] | < +/-3% Full Scale
| 14 | Detection Range | [5 empty] | 0 to 100% LEL with 2 digital Auxiliary switch for L/H alarm signals
| 15 | Repeatability | [5 empty] | <±2% of Full Scale
| 16 | Response time | [5 empty] | <5 Sec
| 17 | Life Time | [5 empty] | More than 5 Years
| 18 | Output Signal | [5 empty] | 4~20 Ma+ Hart (signal+power)
| 19 | System Wiring | [5 empty] | 3 wire
| 20 | Local Indicator LCD Type | [5 empty] | Yes
| 21 | Built-in-Test | [5 empty] | Manual and Automatic
| 22 | Power Supply | [5 empty] | 24 VDC-Loop powered
| 23 | Power Consumption | [5 empty] | VTA (Note 8)
| 24 | Electrical Connection | [5 empty] | M20 x 1.5
| 25 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum(copper free)
| 26 | Mounting | [5 empty] | Bracket (Note 5)
| 27 | Mounting Accessories Material | [5 empty] | 316 SS
| 28 | Degree of Protection | [5 empty] | See Next Page
| 29 | Explosion Protection | [5 empty] | See Next Page
| 30 | Safety Integrity Level | [5 empty] | SIL Rated (Minimum SIL 2)
| 31 | Certificate | [5 empty] | Calibration, SIL, IEC 60529 (IP), ATEX , MATERIAL
| 32 | Nameplates | [5 empty] | Stainless Steel
| 33 | Manufacturer | [5 empty] | VTA
| 34 | Model No. | [5 empty] | VTA
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. The gas detectors shall still work after an extended period in operation ,without any low concentration of the specific gas ,not at all. 3. The response of a detector shall be clearly visible from the outside by a flashing ligh-emitting(LED) of sufficient brightness. 4. The detector shall be designed in such a way that ambient conditions, humidity, temperature and wind can not affect the sensor signal. 5. Vendor scope of supply includes: Sensor, Transmitter, All Mounting Accessories, cable glands,shelter, other accessories (including splash guard, Calibration Kit, etc) 6. Calibration kit contained CALIBRATION GAS, CALIBRATION TOOL, TEST MAGNETS (if required) shall be considered. 7. All devices shall have stainless steel tag plate with their tag no engraved on it which is fixed on the body. 8. Low power consumption to be considered. Quiescence power consumption and alarm power consumption to be specified by vendor. 9. Analogue data with two digital signals as low, high alarm to be sent by detector to F&G system via multicore cable. Also analogue data to be shown by local indicator( LCD) at field. 10. FGDs shall be capable to connect to Smart Hart Communication.
D04

## FGD list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 7 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0016 | D04
FLAMMABLE GAS DETECTOR LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION |  | SERVICE | REMARKS
1 | FGD-1001 | Area 1 - Pig Receiver Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (4 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
2 | FGD-2001 | Area 2 - Slug Catcher System Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
3 | FGD-2002 | Area 2 - Slug Catcher System Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
4 | FGD-2003 | Area 2 - Slug Catcher System Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
5 | FGD-2004 | Area 2 - Slug Catcher System Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
6 | FGD-4001A | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
7 | FGD-4002A | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
8 | FGD-4003A | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
9 | FGD-4004A | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
10 | FGD-4001B | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
11 | FGD-4002B | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
12 | FGD-4003B | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
13 | FGD-4004B | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
14 | FGD-4001C | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
15 | FGD-4002C | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
16 | FGD-4003C | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
17 | FGD-4004C | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
18 | FGD-5001A | Area 5 - 1St. & 2nd Stage Air Cooler Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
19 | FGD-5001B | Area 5 - 1St. & 2nd Stage Air Cooler Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
20 | FGD-5001C | Area 5 - 1St. & 2nd Stage Air Cooler Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
21 | FGD-6001 | Area 6 - Sump & Pig Launcher Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone1, IIB T4 |  | Hydrocarbon
22 | FGD-6002 | Area 6 - Sump & Pig Launcher Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone1, IIB T4 |  | Hydrocarbon
23 | FGD-6003 | Area 6 - Sump & Pig Launcher Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone1, IIB T4 |  | Hydrocarbon
24 | FGD-7001 | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
25 | FGD-7002 | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
26 | FGD-7003 | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
27 | FGD-1101 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 6) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
28 | FGD-1102 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 6) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
29 | FGD-1103 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
30 | FGD-1201 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (3 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
31 | FGD-1202 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (3 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
32 | FGD-1203 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (3 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
33 | Calibration and test device for Flammable Gas Detectors | [12 empty] | NOTE 1
1. Calibration and test devices for Flammable Gas Detectors to be advise by vendor.
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04

## TGD
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 8 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN |  | DT | 0016 | D04
DATASHEET FOR TOXIC GAS DETECTOR
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic, Harsh and Dusty
| 5 | Area Classification | [5 empty] | See Next Page'
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | Function | [5 empty] | Toxic Gas Detector (HC)
| 9 | Service | [5 empty] | See Next Page
| 10 | Detector Type | [5 empty] | Conventional
| 11 | Sensor Type | [5 empty] | electrochemical type
| 12 | Measuring Range / Calibration Range | [5 empty] | 0 - 50 ppm / 5 - 20 ppm
| 13 | Accuracy | [5 empty] | ± 2% of full scale
| 14 | Repeatability | [5 empty] | <±2% of Full Scale
| 15 | Response time | [5 empty] | <5 Sec
| 16 | Life Time | [5 empty] | Typical 2 to 5 Years
| 17 | Output Signal | [5 empty] | 4~20 Ma+ Hart (signal+power)
| 18 | System Wiring | [5 empty] | 3 wire
| 19 | Local Indicator LCD Type | [5 empty] | Yes
| 20 | Built-in-Test | [5 empty] | Manual and Automatic
| 21 | Power Supply | [5 empty] | 24 VDC -Loop Powered
| 22 | Power Consumption | [5 empty] | VTA (Note 8)
| 23 | Electrical Connection | [5 empty] | M20 x 1.5
| 24 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum(copper free)
| 25 | Mounting | [5 empty] | Bracket (Note 5)
| 26 | Mounting Accessories Material | [5 empty] | 316 SS
| 27 | Degree of Protection | [5 empty] | See Next Page
| 28 | Explosion Protection | [5 empty] | See Next Page
| 29 | Safety Integrity Level | [5 empty] | SIL Rated (Minimum SIL 2)
| 30 | Certificate | [5 empty] | Calibration, SIL, IEC 60529 (IP), ATEX , MATERIAL
| 31 | Nameplates | [5 empty] | Stainless Steel
| 32 | Manufacturer | [5 empty] | VTA
| 33 | Model No. | [5 empty] | VTA
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. The gas detectors shall still work after an extended period in operation ,without any low concentration of the specific gas ,not at all. 3. The response of a detector shall be clearly visible from the outside by a flashing ligh-emitting(LED) of sufficient brightness. 4. The detector shall be designed in such a way that ambient conditions, humidity, temperature and wind can not affect the sensor signal. 5. Vendor scope of supply includes: Sensor, Transmitter, All Mounting Accessories, cable glands,shelter, other accessories (including splash guard, Calibration Kit, etc) 6. Calibration kit contained CALIBRATION GAS, CALIBRATION TOOL, TEST MAGNETS (if required) shall be considered. 7. All devices shall have stainless steel tag plate with their tag no engraved on it which is fixed on the body. 8. Low power consumption to be considered. Quiescence power consumption and alarm power consumption to be specified by vendor. 9. Analogue data with two digital signals as low, high alarm to be sent by detector to F&G system via multicore cable. Also analogue data to be shown by local indicator( LCD) at field. 10. TGDs shall be capable to connect to Smart Hart Communication.
D04

## TGD list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 9 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0016 | D04
TOXIC GAS DETECTOR LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION |  | SERVICE | REMARKS
1 | TGD-1001 | Area 1 - Pig Receiver Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (4 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
2 | TGD-2001 | Area 2 - Slug Catcher System Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
3 | TGD-2002 | Area 2 - Slug Catcher System Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
4 | TGD-2003 | Area 2 - Slug Catcher System Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
5 | TGD-2004 | Area 2 - Slug Catcher System Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
6 | TGD-4001A | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
7 | TGD-4002A | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
8 | TGD-4003A | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
9 | TGD-4004A | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
10 | TGD-4001B | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
11 | TGD-4002B | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
12 | TGD-4003B | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
13 | TGD-4004B | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
14 | TGD-4001C | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
15 | TGD-4002C | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
16 | TGD-4003C | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
17 | TGD-4004C | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
18 | TGD-5001A | Area 5 - 1St. & 2nd Stage Air Cooler Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
19 | TGD-5001B | Area 5 - 1St. & 2nd Stage Air Cooler Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
20 | TGD-5001C | Area 5 - 1St. & 2nd Stage Air Cooler Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
21 | TGD-6001 | Area 6 - Sump & Pig Launcher Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone1, IIB T4 |  | Hydrocarbon
22 | TGD-6002 | Area 6 - Sump & Pig Launcher Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone1, IIB T4 |  | Hydrocarbon
23 | TGD-6003 | Area 6 - Sump & Pig Launcher Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone1, IIB T4 |  | Hydrocarbon
24 | TGD-7001 | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
25 | TGD-7002 | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
26 | TGD-7003 | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
27 | TGD-1101 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
28 | TGD-1102 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
29 | TGD-1103 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
30 | TGD-1201 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (3 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
31 | TGD-1202 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (3 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
32 | TGD-1203 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (3 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
33 | Calibration and test device for Toxic Gas Detectors | [12 empty] | NOTE 1
1. Calibration and test devices for Toxic Gas Detectors to be advise by vendor.
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04

## FD
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 10 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN |  | DT | 0016 | D04
DATASHEET FOR FLAME DETECTOR
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 1 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 2 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 3 | Atmospheric Condition | [5 empty] | Non-Acidic, Harsh and Dusty
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 4 | Area Classification | [5 empty] | See Next Page
| 5 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 6 | Function | [5 empty] | Flame Detector
| 7 | Service | [5 empty] | See Next Page
| 8 | Detector Type | [5 empty] | Conventional
| 9 | Sensor Type | [5 empty] | UV/IR
| 10 | Spectral Response | [5 empty] | (VTA)
| 11 | Field of Vision | [5 empty] | max : 120° horizontal, 120° vertical
| 12 | Range (m) | [5 empty] | 20 Meter
| 13 | Sensitive wave length | [5 empty] | VTA
| 14 | Response time | [5 empty] | less than 5 sec @ 50 feet.
| 15 | Output Signal | [5 empty] | 4~20 Ma+ Hart (signal+power)
| 16 | System Wiring | [5 empty] | 3 wire
| 17 | Built-in-Test | [5 empty] | Manual and Automatic (HART Compatible)
| 18 | Power Supply | [5 empty] | 24 VDC-Loop powered
| 19 | Power Consumption | [5 empty] | VTA (Note 5)
| 20 | Electrical Connection | [5 empty] | M20 x 1.5
| 21 | Body and Housing Material | [5 empty] | Enclosure material Epoxy coated die cast aluminum (copper free)
| 22 | Mounting | [5 empty] | Mounting Bracket with Tilt Mount capability
| 23 | Mounting Accessories Material | [5 empty] | 316 SS
| 24 | Degree of Protection | [5 empty] | See Next Page
| 25 | Explosion Protection | [5 empty] | See Next Page
| 26 | Safety Integrity Level | [5 empty] | SIL Rated (Minimum SIL 2)
| 27 | Certificate | [5 empty] | Calibration, SIL ,IEC 60529 (IP), ATEX ,BSI EN54-10(2002)
| 28 | Nameplates | [5 empty] | Stainless Steel
| 30 | Manufacturer | [5 empty] | VTA
| 31 | Model No. | [5 empty] | VTA
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. Vendor scope of supply includes: All Mounting Accessories, cable glands, sunshade, other accessories (including air shield, swivel elbow union, sun and rain protection,etc) and also device shall have self testing ability, IR3 test lamp (with charger),Status Indicator (LED with status, fault and alarm indication) , test magnets (if required). 3. Vendor shall consider specific requirement for proper operation of detector according to ambient humidity if required. 4. All devices shall have stainless steel tag plate with their tag no engraved on it which is fixed on the body. 5. Low power consumption to be considered. Quiescence power consumption and alarm power consumption to be specified by vendor. 6. FDs shall be capable to connect to Smart Hart Communication.
D04

## FD list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 11 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0016 | D04
FLAME DETECTOR LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION |  | SERVICE | REMARKS
1 | FD-2001 | Area 2 - Slug Catcher System Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
2 | FD-2002 | Area 2 - Slug Catcher System Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
3 | FD-2003 | Area 2 - Slug Catcher System Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
4 | FD-3001 | Area 3 - Chemical Package Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (6 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
5 | FD-4001A | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
6 | FD-4002A | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
7 | FD-4003A | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
8 | FD-4004A | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
9 | FD-4001B | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
10 | FD-4002B | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
11 | FD-4003B | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
12 | FD-4004B | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
13 | FD-4001C | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
14 | FD-4002C | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
15 | FD-4003C | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
16 | FD-4004C | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
17 | FD-6001 | Area 6 - Sump & Pig Launcher Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone1, IIB T4 |  | Hydrocarbon
18 | FD-6002 | Area 6 - Sump & Pig Launcher Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone1, IIB T4 |  | Hydrocarbon
19 | FD-8001 | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (11 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
20 | FD-8002 | Area 9 - Diesel Generator Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (11 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon
21 | Calibration and test device for Flame Detectors | [12 empty] | NOTE 1
1. Calibration and test devices for Flame Detectors to be advise by vendor.
D04
D04
D04
D04

## HORN
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 12 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN |  | DT | 0016 | D04
DATASHEET FOR HORN
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic, Harsh and Dusty
| 5 | Area Classification | [5 empty] | See Next Page
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | System Type | [5 empty] | See Next Page
| 9 | Function | [5 empty] | Local Alarm with 2 modes: non-continuous for flammable and toxic gas detection low alarm • Continuous for fire detection & for flammable and toxic gas detection high alarm
| 10 | Sound Level | [5 empty] | not exceed 120dB (A) at 1 meter distance (VTA)
| 11 | Service | [5 empty] | Hydrocarbon
| 12 | Adjustable Sound Intensity | [5 empty] | Yes
| 13 | Frequency Range | [5 empty] | VTA
| 14 | Multiple Terminal Connection | [5 empty] | Required
| 15 | No. of Selectable Tones | [5 empty] | Minimum 2
| 16 | Power Supply | [5 empty] | 24 VDC-Loop powered
| 17 | System Wiring | [5 empty] | 5 Core x 1.5
| 18 | Power Consumption | [5 empty] | VTA (Note 4)
| 19 | Electrical Connection | [5 empty] | M25 x 1.5(Note 9 )
| 20 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum (copper free).
| 21 | Installation | [5 empty] | Fix
| 22 | Mounting | [5 empty] | Bracket (Note 2)
| 23 | Mounting Accessories Material | [5 empty] | 316 SS
| 24 | Degree of Protection | [5 empty] | IP 65
| 25 | Explosion Protection | [5 empty] | Eexd
| 26 | Weather Proof and Dust Proof | [5 empty] | Yes
| 27 | Safety Integrity Level | [5 empty] | Non SIL
| 28 | Certificate | [5 empty] | IEC 60529 (IP), ATEX , BSI EN54-3
| 29 | Nameplates Material | [5 empty] | Stainless Steel
| 30 | Manufacturer | [5 empty] | VTA
| 31 | Model No. | [5 empty] | VTA
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. Vendor shall specify weight, color and dimentions of devices and accessories. 3. The value of End Of Line (EOL) resistor shall be suggested by vendor. 4. Mounting Accessories, sunshade and cable gland are included in vendor scope of supply. 5. 2 different tones one for Flammable/ Toxic gas detection (non-continuous) and one for fire detection (continuous). Each tone shall be activated by receiveing dedicated signal. 6. All devices shall have stainless steel tag plate with their tag no engraved on it which is fixed on the body. 7. Low power consumption to be considered. Quiescence power consumption and alarm power consumption to be specified by vendor. 8. Horn alarms shall have a range of at least 1.5 km in still air. 9.Junction box(EXE type with 7 aurmored output cable) for each conventional Horns &related beacons and cable gland for connection to junction box are included in vendor scope of supply. (All internal termination cabling in between shall be done by vendor.)
D04
D04

## HORN list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 13 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0016 | D04
HORN LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION |  | SERVICE | REMARKS
1 | HN-1001 | Area 1 - Pig Receiver Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
2 | HN-2001 | Area 2 - Slug Catcher System Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
3 | HN-3001 | Area 3 - Chemical Package Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
4 | HN-4001 | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
5 | HN-4002 | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
6 | HN-5001 | Area 5 - 1St. & 2nd Stage Air Cooler Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
7 | HN-6001 | Area 6 - Sump & Pig Launcher Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
8 | HN-7002 | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
9 | HN-8001 | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
10 | HN-9001 | Area 9 - Diesel Generator Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
11 | HN-1101 | Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Addressable
12 | HN-1201 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (4 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Addressable
13 | HN-1202 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (5 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Addressable
14 | HN-1301 | CCTV Control Room |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (6 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Addressable
15 | HN-1401 | Ware house |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (7 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Addressable
16 | Calibration and test device for Horn | [12 empty] | NOTE 1
1. Calibration and test devices for Horn to be advise by vendor.
D04
D04
D04
D04
D04
D04
D04

## BB-BR
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 14 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN |  | DT | 0016 | D04
DATASHEET FOR BEACON
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic, Harsh and Dusty
| 5 | Area Classification | [5 empty] | See Next Page
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | System Type | [5 empty] | Conventional/ Addressable
| 9 | Service | [5 empty] | See Next Page
| 10 | Function | [5 empty] | • Red for fire detection • Blue for Toxic Gas Detector(if applicable) • Yellow for flammable gas detection
| 11 | Flash Rate | [5 empty] | 60 FPM/1HZ (VTA)
| 12 | Colour | [5 empty] | See Next Page
| 13 | Lens Type | [5 empty] | Glass
| 14 | Field of View | [5 empty] | 360°
| 15 | Tube type | [5 empty] | Xenon
| 16 | Effective Intensity | [5 empty] | 200 cd to 1000 cd candela (VTA)
| 17 | Power Supply | [5 empty] | 24 VDC-Loop powered
| 18 | System Wiring | [5 empty] | 2 Core x 1.5 (for each Blue/ Red/Yellow Beacon)
| 19 | Power Consumption | [5 empty] | VTA (Note 4)
| 20 | Electrical Connection | [5 empty] | M20 x 1.5
| 21 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum (copper free)
| 22 | Installation | [5 empty] | Fix
| 23 | Mounting | [5 empty] | Bracket for outdoor and wall mounted for indoor type (Note 2)
| 24 | Mounting Accessories Material | [5 empty] | 316 SS
| 25 | Degree of Protection | [5 empty] | See Next Page
| 26 | Explosion Protection | [5 empty] | See Next Page
| 27 | Weather Proof and Dust Proof | [5 empty] | Yes
| 28 | Safety Integrity Level | [5 empty] | Non SIL
| 29 | Certificate | [5 empty] | IEC 60529 (IP), ATEX , BSI EN54-3
| 30 | Body Color | [5 empty] | • Red for fire and flammable gas detection • Red for Toxic Gas Detector(if applicable)
| 31 | Nameplates Material | [5 empty] | Stainless Steel
| 32 | Manufacturer | [5 empty] | VTA
| 33 | Model No. | [5 empty] | VTA
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. Vendor shall specify weight, color and dimentions of devices and accessories. 3. The value of End Of Line (EOL) resistor shall be suggested by vendor. 4. Mounting Accessories, sunshade and cable gland are included in vendor scope of supply. 5. 3 different colors to be selected for lights of beacon: '• Red for fire detection • Blue for Toxic Gas Detector(if applicable) • Yellow for flammable gas detection 6. All devices shall have stainless steel tag plate with their tag no engraved on it which is fixed on the body. 7. Low power consumption to be considered. Quiescence power consumption and alarm power consumption to be specified by vendor.

## BB-BR list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 15 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0016 | D04
BEACON LIST
ITEM | TAG NO. | LOCATION |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION | COLOR | SERVICE | REMARKS
1 | BB-1001 | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Blue | Hydrocarbon | Conventional
2 | BB-2001 | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Blue | Hydrocarbon | Conventional
3 | BB-3001 | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Blue | Hydrocarbon | Conventional
4 | BB-4001 | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Blue | Hydrocarbon | Conventional
5 | BB-4002 | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Blue | Hydrocarbon | Conventional
6 | BB-5001 | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Blue | Hydrocarbon | Conventional
7 | BB-6001 | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Blue | Hydrocarbon | Conventional
8 | BB-7002 | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Blue | Hydrocarbon | Conventional
9 | BB-8001 | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Blue | Hydrocarbon | Conventional
10 | BB-9001 | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Blue | Hydrocarbon | Conventional
11 | BB-1101 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Blue | Hydrocarbon | Adressable
12 | BB-1201 | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Blue | Hydrocarbon | Adressable
13 | BB-1202 | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Blue | Hydrocarbon | Adressable
14 | BB-1301 | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Blue | Hydrocarbon | Adressable
15 | BB-1401 | Ware house |  | BK-GCS-PEDCO-120-IN-PY-0006 (7 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Blue | Hydrocarbon | Adressable
16 | BR-1001 | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Red | Hydrocarbon | Conventional
17 | BR-2001 | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Red | Hydrocarbon | Conventional
18 | BR-3001 | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Red | Hydrocarbon | Conventional
19 | BR-4001 | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Red | Hydrocarbon | Conventional
20 | BR-4002 | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Red | Hydrocarbon | Conventional
21 | BR-5001 | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Red | Hydrocarbon | Conventional
22 | BR-6001 | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Red | Hydrocarbon | Conventional
23 | BR-7002 | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Red | Hydrocarbon | Conventional
24 | BR-8001 | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Red | Hydrocarbon | Conventional
25 | BR-9001 | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Red | Hydrocarbon | Conventional
26 | BR-1101 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Red | Hydrocarbon | Adressable
27 | BR-1103 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7) |  | Indoor |  | IP 54 |  | Unclassified | Red | Hydrocarbon | Adressable
28 | BR-1201 | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Red | Hydrocarbon | Adressable
29 | BR-1202 | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Red | Hydrocarbon | Adressable
30 | BR-1301 | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Red | Hydrocarbon | Adressable
31 | BR-1401 | Ware house |  | BK-GCS-PEDCO-120-IN-PY-0006 (7 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Red | Hydrocarbon | Adressable
32 | BY-1001 | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Yellow | Hydrocarbon | Conventional
33 | BY-2001 | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Yellow | Hydrocarbon | Conventional
34 | BY-3001 | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Yellow | Hydrocarbon | Conventional
35 | BY-4001 | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Yellow | Hydrocarbon | Conventional
36 | BY-4002 | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Yellow | Hydrocarbon | Conventional
37 | BY-5001 | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Yellow | Hydrocarbon | Conventional
38 | BY-6001 | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Yellow | Hydrocarbon | Conventional
39 | BY-7002 | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Yellow | Hydrocarbon | Conventional
40 | BY-8001 | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Yellow | Hydrocarbon | Conventional
41 | BY-9001 | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Yellow | Hydrocarbon | Conventional
42 | BY-1101 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Yellow | Hydrocarbon | Adressable
43 | BY-1201 | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Yellow | Hydrocarbon | Adressable
44 | BY-1202 | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Yellow | Hydrocarbon | Adressable
45 | BY-1301 | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Yellow | Hydrocarbon | Adressable
46 | BY-1401 | Ware house |  | BK-GCS-PEDCO-120-IN-PY-0006 (7 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 | Yellow | Hydrocarbon | Adressable
47 | calibration and test device for Beacons | [11 empty] | NOTE 1
1. Calibration and test devices for Beacons to be advise by vendor.
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04

## HGD
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 16 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN |  | DT | 0016 | D04
DATASHEET FOR HYDROGEN GAS DETECTOR
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic, Harsh and Dusty
| 5 | Area Classification | [5 empty] | See Next Page
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | System Type | [5 empty] | Conventional
| 9 | Function | [5 empty] | Hydrogen Gas Detector
| 10 | Service | [5 empty] | See Next Page
| 11 | Sensor Type | [5 empty] | CatalyticType (HGD)
| 12 | Measuring Range/Calibration Range | [5 empty] | VTA/ 0 - 100% LEL
| 13 | Accuracy | [5 empty] | <+/-2 ppm
| 14 | Life Time | [5 empty] | Typical 2 to 5 Years
| 15 | Response time | [5 empty] | < 5 Seconds
| 16 | Alarm Range | [5 empty] | High Level :5% LEL , High High Level:10% LEL
| 17 | Repeatability | [5 empty] | VTA
| 18 | Output Signal | [5 empty] | 4~20 Ma+ Hart (signal+power)
| 19 | Power Supply | [5 empty] | 24 VDC-Loop powered
| 20 | System Wiring | [5 empty] | 3 wire
| 21 | Power Consumption | [5 empty] | VTA (Note 8)
| 22 | Electrical Connection | [5 empty] | M20 x 1.5
| 23 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum (copper free)
| 24 | Installation | [5 empty] | Fix
| 25 | Mounting | [5 empty] | Bracket (Note 5)
| 26 | Mounting Accessories Material | [5 empty] | 316 SS
| 27 | Degree of Protection | [5 empty] | See Next Page
| 28 | Explosion Protection | [5 empty] | See Next Page
| 29 | Weather Proof and Dust Proof | [5 empty] | Yes
| 30 | Safety Integrity Level | [5 empty] | Non SIL
| 31 | Certificate | [5 empty] | Calibration, SIL, IEC 60529 (IP), ATEX , MATERIAL
| 32 | Nameplates Material | [5 empty] | Stainless Steel
| 33 | Manufacturer | [5 empty] | VTA
| 34 | Model No. | [5 empty] | VTA
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. The gas detectors shall still work after an extended period in operation ,without any low concentration of the specific gas ,none at all. 3. The response of a detector shall be clearly visible from the outside by a flashing ligh-emitting(LED) of sufficient brightness. 4. The detector shall be designed in such a way that ambient conditions, humidity, temperature and wind can not affect the sensor signal. 5. Vendor scope of supply includes: Sensor, Transmitter, All Mounting Accessories, cable glands, other accessories (including splash guard, Calibration Kit, etc) 6.Calibration kit contained CALIBRATION GAS, CALIBRATION TOOL, TEST MAGNETS (if required) shall be considered. 7. All devices shall have stainless steel tag plate with their tag no engraved on it which is fixed on the body. 8. Low power consumption to be considered. Quiescence power consumption and alarm power consumption to be specified by vendor. 9. HGDs shall be capable to connect to Smart Hart Communication. 10. The VENDOR shall provide the zero stability and the drift of the full-scale sensitivity, in % LFL (for Catalytic GD), per month and year,

## HGD list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 17 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0016 | D04
HYDROGEN GAS DETECTOR LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION |  | SERVICE | REMARKS
1 | HGD-1101 | Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7) |  | Indoor |  | IP 65 |  | Eexd 'Zone1, IIC T4 |  | Hydroen (related to the batteries)
2 | HGD-1102 | Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7) |  | Indoor |  | IP 65 |  | Eexd 'Zone1, IIC T4 |  | Hydroen (related to the batteries)
5 | calibration and test device for HGDs | [12 empty] | NOTE 1
1. Calibration and test devices for HGDs to be advise by vendor.
D04

## MAC
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 18 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN |  | DT | 0016 | D04
DATASHEET FOR MANUAL ALARM CALL POINT
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic, Harsh and Dusty
| 5 | Area Classification | [5 empty] | See Next Page
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | Function | [5 empty] | Manual Alarm
| 9 | Service | [5 empty] | See Next Page
| 10 | Glass Type | [5 empty] | Resettable type
| 11 | Switch Type | [5 empty] | Single pole, Normally Closed و Hermetically Sealed (equipped with opening key for test, maintenance and reset)
| 12 | Detector Type | [5 empty] | Conventional/Addressable
| 13 | Alarm Indicator | [5 empty] | High Intensity Red LED
| 14 | Output Signal | [5 empty] | Voltage Free Contact (24VDC,5A)
| 15 | System Wiring | [5 empty] | 2 Core
| 16 | Test Key | [5 empty] | Required
| 17 | Power Supply | [5 empty] | 24 VDC-Loop powered
| 18 | Electrical Connection | [5 empty] | M20 x 1.5
| 19 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum (copper free)
| 20 | Colour | [5 empty] | Red With Black Marking Colour
| 21 | End of Line Resistor | [5 empty] | Yes
| 22 | Mounting | [5 empty] | Bracket (Note 2)
| 23 | Mounting Accessories Material | [5 empty] | 316 SS
| 24 | Degree of Protection | [5 empty] | See Next Page
| 25 | Explosion Protection | [5 empty] | See Next Page
| 26 | Safety Integrity Level | [5 empty] | Non SIL
| 27 | Certificate | [5 empty] | IEC 60529 (IP), ATEX , BSI EN54-11
| 28 | Nameplates Material | [5 empty] | Stainless Steel
| 29 | Manufacturer | [5 empty] | VTA
| 30 | Model No. | [5 empty] | VTA
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. Mounting Accessories, cable gland,sunshade are included in vendor scope of supply. 3. All devices shall have stainless steel tag plate with their tag no engraved on it which is fixed on the body.

## MAC list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 19 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0016 | D04
MANUAL ALARM CALL POINT LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION |  | SERVICE | REMARKS
1 | MAC-1001 | Area 1 - Pig Receiver Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
2 | MAC-1002 | Area 1 - Pig Receiver Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
3 | MAC-2001 | Area 2 - Slug Catcher System Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
4 | MAC-2002 | Area 2 - Slug Catcher System Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
5 | MAC-2003 | Area 2 - Slug Catcher System Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
6 | MAC-3001 | Area 3 - Chemical Package Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
7 | MAC-4001 | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
8 | MAC-4002 | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
9 | MAC-5001 | Area 5 - 1St. & 2nd Stage Air Cooler Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
10 | MAC-5002 | Area 5 - 1St. & 2nd Stage Air Cooler Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
11 | MAC-6001 | Area 6 - Sump & Pig Launcher Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
12 | MAC-6002 | Area 6 - Sump & Pig Launcher Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
13 | MAC-7001 | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
14 | MAC-7002 | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
15 | MAC-8001 | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
16 | MAC-8002 | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
17 | MAC-8003 | Area 8 - Fuel Oil Storage Drum & Fire Water Storage Tanks& Air Compressor /Air Dryer Packages Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
18 | MAC-9001 | Area 9 - Diesel Generator Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
19 | MAC-1101 | Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7) |  | Outdoor |  | IP 65 |  | Eexd 'Zone1, IIC T4 |  | Hydroen (related to the batteries) | Conventional
20 | MAC-1102 | Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7) |  | Indoor |  | IP 54 |  | Unclassified |  | Hydrocarbon | Addressable
21 | MAC-1103 | Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7) |  | Indoor |  | IP 54 |  | Unclassified |  | Hydrocarbon | Addressable
22 | MAC-1104 | Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7) |  | Indoor |  | IP 54 |  | Unclassified |  | Hydrocarbon | Addressable
23 | MAC-1105 | Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7) |  | Indoor |  | IP 54 |  | Unclassified |  | Hydrocarbon | Addressable
24 | MAC-1201 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (4 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Addressable
25 | MAC-1202 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (4 of 7) |  | Indoor |  | IP 54 |  | Unclassified |  | Hydrocarbon | Addressable
26 | MAC-1203 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (5 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Addressable
27 | MAC-1301 | CCTV Control Room |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (6 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Addressable
28 | MAC-1302 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (6 of 7) |  | Indoor |  | IP 54 |  | Unclassified |  | Hydrocarbon | Addressable
29 | MAC-1401 | Ware house |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (7 of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Addressable
30
31
32 | calibration and test device for MACs | [12 empty] | NOTE 1
1. Calibration and test devices for MACs to be advise by vendor.
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04

## LHD
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 20 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN |  | DT | 0016 | D04
DATASHEET FOR LINEAR HEAT DETECTOR
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic, Harsh and Dusty
| 5 | Area Classification | [5 empty] | See Next Page
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | Detector Type | [5 empty] | Addressable/ 'Conventional
| 9 | Function | [5 empty] | Heat Detection
| 10 | Service | [5 empty] | See Next Page
| 11 | Sensor Type | [5 empty] | Two Twisted Steel Conductors with Heat Sensitive Polymer Coated
| 12 | Outer Sheath Material | [5 empty] | PVC or Chemical Resistant Nylon (VTA)
| 13 | Overall Diameter (mm) | [5 empty] | 3.5 ~ 4.5 mm (VTA)
| 14 | Alarm Temperature | [5 empty] | 85°C
| 15 | Temperature Rise | [5 empty] | 8 °C Perminute
| 16 | Cable Lentgh | [5 empty] | 15 m(VTA)
| 17 | Output Signal | [5 empty] | Digital 0-24VDC
| 18 | Power Supply | [5 empty] | 24 VDC-Loop powered
| 19 | System Wiring | [5 empty] | 2 Core x 1.5
| 20 | Electrical Connection | [5 empty] | M20 x 1.5
| 21 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum (copper free)
| 22 | Installation | [5 empty] | Fix
| 23 | Mounting | [5 empty] | Electrical Transformer Surface Mounted
| 24 | Mounting Accessories Material | [5 empty] | VTA
| 25 | Degree of Protection | [5 empty] | See Next Page
| 26 | Explosion Protection | [5 empty] | See Next Page
| 27 | Weather Proof and Dust Proof | [5 empty] | Yes
| 28 | Safety Integrity Level | [5 empty] | Non SIL
| 29 | Certificate | [5 empty] | IEC 60529 (IP), ATEX , MATERIAL
| 30 | Nameplates Material | [5 empty] | Stainless Steel
| 31 | Manufacturer | [5 empty] | VTA
| 32 | Model No. | [5 empty] | VTA
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. Mounting Accessories, shelter and cable gland are included in vendor scope of supply. 3. All devices shall have stainless steel tag plate with their tag no. engraved on it which is fixed on the body. 4. All required mounting & Termination accessories to be provided by vendor. 9.Junction box (EXE type) as per Linear Heat detectors and internal cabling/cable gland for connection to junction box are included in vendor scope of supply.
D04

## LHD list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 21 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0016 | D04
LINEAR HEAT DETECTOR LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION |  | SERVICE | REMARKS
1 | LHD-7001 | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
2 | LHD-7002 | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Conventional
3 | LHD-1201 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (5of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Addressable
4 | LHD-1202 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (5of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Addressable
5 | LHD-1203 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (5of 7) |  | Outdoor |  | IP 65 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Addressable
6
7
8
9
10
11
12
13
14
15
16
17
18
19 | calibration and test device for LHDs | [12 empty] | NOTE 1
1. Calibration and test devices for LHDs to be advise by vendor.
D04
D04
D04

## SD
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 22 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN |  | DT | 0016 | D04
DATASHEET FOR SMOKE DETECTOR/HEAT & SMOKE DETECTOR
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic
| 5 | Area Classification | [5 empty] | See Next Page
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | Detector Type | [5 empty] | Addressable
| 9 | Function | [5 empty] | Smoke Detector
| 10 | Service | [5 empty] | False floor/'False ceiling / Ceiling smoke detection
| 11 | Sensor Type | [5 empty] | Smoke Sensing Element : Optical type(scattered-light type or transmitted-light type detectors)
| 12 | Rate of Rise(ROR) | [5 empty] | Yes (Temperature Rise: 8 °C Perminute )
| 13 | Built-in-Test | [5 empty] | Manual
| 14 | Area Coverage | [5 empty] | 50 m²
| 15 | Operating Temprature | [5 empty] | -10 ºC to 90 ºC
| 16 | Alarm Set point | [5 empty] | VTC
| 17 | Output Signal | [5 empty] | VTA
| 18 | Power Supply | [5 empty] | 24 VDC-Loop powered
| 19 | System Wiring | [5 empty] | 2 Core x 1.5
| 20 | Contact Type & Rating | [5 empty] | 24 VDC, DPDT
| 21 | Power Consumption | [5 empty] | VTA (Note 7)
| 22 | Electrical Connection | [5 empty] | M20 x 1.5
| 23 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum (copper free)
| 24 | Installation | [5 empty] | Fix
| 25 | Sampling Frequency | [5 empty] | VTA
| 26 | Mounting | [5 empty] | Under false floor/ Ceiling (Note 6)
| 27 | Mounting Accessories Material | [5 empty] | VTA
| 28 | Degree of Protection | [5 empty] | See Next Page
| 29 | Explosion Protection | [5 empty] | See Next Page
| 30 | Weather Proof and Dust Proof | [5 empty] | Yes
| 31 | Safety Integrity Level | [5 empty] | Non SIL
| 32 | Certificate | [5 empty] | IEC 60529 (IP), ATEX , MATERIAL
| 33 | Sensitivity Adjustable Required | [5 empty] | Yes
| 34 | Indicator | [5 empty] | 2 LED Indication for local display and also a Remote Indicator for False Ceiling / False Floor application.
| 35 | Nameplates Material | [5 empty] | Stainless Steel
| 36 | Manufacturer | [5 empty] | VTA
| 37 | Model No. | [5 empty] | VTA
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. Detectors shall have an inherently stable operation with built in compensation being impaired by dust, dirt or humidity. 3. All circuity must be protected against electrical trasients and electromagnetic interferences. 4. Faulty zone wiring shall not damage the detector. 5. A Built in barrier shall prevent entry of insects in the sensors. 6. Mounting Accessories, cable gland, end of line resistor are included in vendor scope of supply. 7. Low power consumption to be considered. Quiescence power consumption and alarm power consumption to be specified by vendor. 8. Remote Indicator For False Ceiling /False Floor Smoke detector shall be considered.

## SD list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 23 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0016 | D04
SMOKE DETECTOR LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION |  | REMARKS
1 | SD-1101 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
2 | SD-1102 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
3 | SD-1103 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
4 | SD-1104 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
5 | SD-1105 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
6 | SD-1106 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
7 | SD-1107 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
8 | SD-1108 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
9 | SD-1109 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
10 | SD-1110 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
11 | SD-1111 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
12 | SD-1112 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
13 | SD-1113 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
14 | SD-1114 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
15 | SD-1115 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
16 | SD-1116 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
17 | SD-1117 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
18 | SD-1118 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
19 | SD-1119 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
20 | SD-1120 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
21 | SD-1121 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
22 | SD-1122 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
23 | SD-1123 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
24 | SD-1124 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
25 | SD-1125 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
26 | SD-1126 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
27 | SD-1127 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
28 | SD-1128 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
29 | SD-1129 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
30 | SD-1130 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
31 | SD-1131 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
32 | SD-1132 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
33 | SD-1133 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
34 | SD-1134 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
35 | SD-1135 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
36 | SD-1136 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7 |  | Indoor |  | IP 54 |  | Unclassified
37 | SD-1201 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (4 of 7) |  | Indoor |  | IP 54 |  | Unclassified
38 | SD-1202 | Extension of Existing Elect. Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (4 of 7) |  | Indoor |  | IP 54 |  | Unclassified
39 | SD-1203 | Extension of Existing Elect. Building-False Floor |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (4 of 7) |  | Indoor |  | IP 54 |  | Unclassified
40 | SD-1204 | Extension of Existing Elect. Building-False Floor |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (4 of 7) |  | Indoor |  | IP 54 |  | Unclassified
41 | SD-1301 | CCTV Control Room |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (6 of 7) |  | Indoor |  | IP 54 |  | Unclassified
42 | SD-1302 | CCTV Control Room |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (6 of 7) |  | Indoor |  | IP 54 |  | Unclassified
43 | SD-1303 | CCTV Control Room |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (6 of 7) |  | Indoor |  | IP 54 |  | Unclassified
44 | SD-1304 | CCTV Control Room |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (6 of 7) |  | Indoor |  | IP 54 |  | Unclassified
45 | SD-1401 | Ware house |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (7 of 7) |  | Indoor |  | IP 54 |  | Unclassified
46 | SD-1402 | Ware house |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (7 of 7) |  | Indoor |  | IP 54 |  | Unclassified
47 | SD-1403 | Ware house |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (7 of 7) |  | Indoor |  | IP 54 |  | Unclassified
48 | calibration and test device for SDs | [12 empty] | NOTE 1
1. Calibration and test devices for SDs to be advise by vendor.
D04

## BL
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 24 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN |  | DT | 0016 | D04
DATASHEET FOR BELL
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic, Harsh and Dusty
| 5 | Area Classification | [5 empty] | See Next Page
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | System Type | [5 empty] | See Next Page
| 9 | Sound Pressure Level | [5 empty] | 80 dB (At 1 meter) (VTA)
| 10 | Service | [5 empty] | See Next Page
| 11 | Adjustable Sound Intensity | [5 empty] | Yes
| 12 | Adjustable Sound In Intensity | [5 empty] | Yes
| 13 | No. of Selectable Tones | [5 empty] | Minimum 2
| 14 | Power Supply | [5 empty] | 24 VDC-Loop powered
| 15 | System Wiring | [5 empty] | 2 Core x 1.5
| 16 | Power Consumption | [5 empty] | VTA (Note 4)
| 17 | Electrical Connection | [5 empty] | M25 x 1.5
| 18 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum (copper free)
| 19 | Installation | [5 empty] | Fix
| 20 | Mounting | [5 empty] | Wall mounted (Note 2)
| 21 | Mounting Accessories Material | [5 empty] | 316 SS
| 22 | Degree of Protection | [5 empty] | See Next Page
| 23 | Explosion Protection | [5 empty] | See Next Page
| 24 | Weather Proof and Dust Proof | [5 empty] | Yes
| 25 | Safety Integrity Level | [5 empty] | Non SIL
| 26 | Certificate | [5 empty] | IEC 60529 (IP), ATEX , BSI EN54-3
| 27 | Nameplates Material | [5 empty] | Stainless Steel
| 28 | Manufacturer | [5 empty] | VTA
| 29 | Model No. | [5 empty] | VTA
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. Vendor shall specify weight, color and dimentions of devices and accessories. 3. Mounting Accessories, sunshade and cable gland are included in vendor scope of supply. 4. All devices shall have stainless steel tag plate with their tag no engraved on it which is fixed on the body. 5. Low power consumption to be considered. Quiescence power consumption and alarm power consumption to be specified by vendor.

## BL list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 25 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0016 | D04
BELL LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION |  | SERVICE | REMARKS
1 | BL-1101 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (2 of 7) |  | Indoor |  | IP 54 |  | Unclassified |  | Hydrocarbon | Addressable
3
4
5
6
7
8
9
10
11
12
13
14
15 | calibration and test device for Bells | [12 empty] | NOTE 1
1. Calibration and test devices for Bells to be advise by vendor.

## HD
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 26 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN |  | DT | 0016 | D04
DATASHEET FOR HEAT DETECTOR
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic
| 5 | Area Classification | [5 empty] | See Next Page
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | Detector Type | [5 empty] | See Next Page
| 9 | Function | [5 empty] | Heat Detector
| 10 | Service | [5 empty] | Ceiling heat detection
| 11 | Sensor Type | [5 empty] | Heat Sensing Element: Fusible Alloy Silver Contact
| 12 | Rate of Rise(ROR) | [5 empty] | Yes (Temperature Rise: 8 °C Perminute )
| 13 | Built-in-Test | [5 empty] | Manual
| 14 | Area Coverage | [5 empty] | 37 m²
| 15 | Operating Temprature | [5 empty] | -10 ºC to 90 ºC
| 16 | Alarm Set point | [5 empty] | VTC
| 17 | Output Signal | [5 empty] | VTA
| 18 | Power Supply | [5 empty] | 24 VDC-Loop powered
| 19 | System Wiring | [5 empty] | 2 Core x 1.5
| 20 | Contact Type & Rating | [5 empty] | 24 VDC, DPDT
| 21 | Power Consumption | [5 empty] | VTA (Note 7)
| 22 | Electrical Connection | [5 empty] | M20 x 1.5
| 23 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum (copper free)
| 24 | Installation | [5 empty] | Fix
| 25 | Sampling Frequency | [5 empty] | VTA
| 26 | Mounting | [5 empty] | Under false Ceiling (Note 6)
| 27 | Mounting Accessories Material | [5 empty] | VTA
| 28 | Degree of Protection | [5 empty] | See Next Page
| 29 | Explosion Protection | [5 empty] | See Next Page
| 30 | Weather Proof and Dust Proof | [5 empty] | Yes
| 31 | Safety Integrity Level | [5 empty] | Non SIL
| 32 | Certificate | [5 empty] | IEC 60529 (IP), ATEX , MATERIAL
| 33 | Sensitivity Adjustable Required | [5 empty] | Yes
| 34 | Indicator | [5 empty] | 2 LED Indication for local display and also a Remote Indicator for False Ceiling / False Floor application.
| 35 | Nameplates Material | [5 empty] | Stainless Steel
| 36 | Manufacturer | [5 empty] | VTA
| 37 | Model No. | [5 empty] | VTA
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. Detectors shall have an inherently stable operation with built in compensation being impaired by dust, dirt or humidity. 3. All circuity must be protected against electrical trasients and electromagnetic interferences. 4. Faulty zone wiring shall not damage the detector. 5. A Built in barrier shall prevent entry of insects in the sensors. 6. Mounting Accessories, cable gland, end of line resistor are included in vendor scope of supply. 7. Low power consumption to be considered. Quiescence power consumption and alarm power consumption to be specified by vendor. 8. Remote Indicator For False Ceiling /False Floor Heat detector shall be considered.

## HD list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR F&G DETECTORS & EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 27 از 27
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0016 | D04
HEAT DETECTOR LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION |  | SERVICE | REMARKS
1 | HD-1101 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (6 OF 7) |  | Indoor |  | IP 65 |  | Eexd 'Zone1, IIC T4 |  | Hydroen (related to the batteries) | Conventional
2 | HD-1102 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (6 OF 7) |  | Indoor |  | IP 65 |  | Eexd 'Zone1, IIC T4 |  | Hydroen (related to the batteries) | Conventional
3 | HD-1301 | Extension of Existing Control Building |  |  | BK-GCS-PEDCO-120-IN-PY-0006 (6 OF 7) |  | Indoor |  | IP 54 |  | Eexd Zone2, IIB T4 |  | Hydrocarbon | Addressable
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18 | calibration and test device for LHDs | [12 empty] | NOTE 1
1. Calibration and test devices for LHDs to be advise by vendor.
D04
D04